## 6th Iteration
Preparation of a Solids Mass Balance for 32.4 MLD GWWTP in Kathmandu
1 | Definition of terms
BODC = biochemical oxygen demand expressed as a concentration, g/m3
BODM = biochemical oxygen demand expressed as a mass, kg/d
TSSC = total suspended solids expressed as a concentration, g/m3
TSSM = total suspended solids expressed as a mass, kg/d
2 | Wastewater flowrates
a. | Annual average flowrate | [5 empty] | 32400 | m3/d
b. | Return Flowrate | [5 empty] | 411.8883 | m3/d
c. | Total average flowrate = | [5 empty] | 32811.8883 | m3/d
3 | Influent characteristics | [10 empty] | Legend
a. | BODC = | [5 empty] | 300 | g/m3 |  |  |  |  | Real Values Taken From WWTP
b. | TSSC = | [5 empty] | 400 | g/m3 |  |  |  |  | Values taken from Metcalf & Eddy
c. | Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67% | [5 empty] | Computed Values
| TSS removed in grit = | [5 empty] | 5% | [5 empty] | Referenced Values
d. | TSSC after grit removal = | [5 empty] | 380 | g/m3
e. | Assume Volatile fraction of grit = | [5 empty] | 3%
| Specific Gravity of Grit = | [5 empty] | 2.65 | kg/m3
| Solids Concentration in Grit = | [5 empty] | 1%
4 | Sludge and biosolids characteristics
a. | Concentration of primary sludge = | [5 empty] | 4%
b. | Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
c. | (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
d. | Total suspended solids in digested sludge = | [5 empty] | 5%
e. | Special Gravity of Solids = | [5 empty] | 1
f. | Fraction of the biological solids that are biodegradable = | [5 empty] | 65%
g. | The value of BODC can be obtained by multiplying the value of UBOD by a factor of | [5 empty] | 0.68
5 | Effluent characteristics
a. | BODC = | [5 empty] | 10 | g/m3
b. | TSSC = | [5 empty] | 10 | g/m3
Secondary Clarifier Outlet characteristics
c. | BODC = | [5 empty] | 20 | g/m3
d. | TSSC = | [5 empty] | 30 | g/m3
6 | Primary clarifier
Assumtions,
a. | BOD removal= | [5 empty] | 33%
b. | TSS removal = | [5 empty] | 50%
c. | VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
7 | Secondary treatment
Assumption,
a. | The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
b. | Aeration tank volume, Vr = | [5 empty] | 7900 | m3
c. | Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
d. | Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
e. | Solids Retention Time, SRT = | [5 empty] | 10 | d
f. | MLSS in Return Activated Sludge= | [5 empty] | 7000 | g/m3
8 | Sludge digestion
Assumption,
a. | SRT = | [5 empty] | 20 | d
b. | Volatile Solids Reduction, VSR = | [5 empty] | 60%
d. | BODC in digester supernatant = | [5 empty] | 1000 | g/m3
e. | TSSC in digested sludge = | [5 empty] | 5%
f. | Yield Coefficient, Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized
g. | Endogenous coefficient, b = | [5 empty] | 0.03 | d-1
9 | Sludge dewatering
Assumptions,
a. | Sludge cake = | [5 empty] | 22% | solids
b. | Specific gravity of sludge = | [5 empty] | 1.123
c. | Solids capture = | [5 empty] | 90%
d. | Centrate BODC = | [5 empty] | 2000 | mg/L
10 | Other Important Values
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| TSSC of Supernatant = | [5 empty] | 0.5%
| Density of Water = | [5 empty] | 1000 | kg/m3
SOLUTION
1 | Convert the given constitient quantities to daily mass values
a. | BODM in influent :
| BODM = | [5 empty] | 9720 | kg/d | {(m3/d* g/m3) /(g/kg)}
| BODM of return flow = | [5 empty] | 879.4575 | kg/d
| BODM total = | [5 empty] | 10599.4575 | kg/d
b | TSSM in influent
| TSSM = | [5 empty] | 12960 | kg/d | {(m3/d* g/m3) /(g/kg)}
| TSSM of return flow = | [5 empty] | 1898.7847 | kg/d
| TSSM of combined flow = | [5 empty] | 14858.7847 | kg/d
c. | TSSM removed in grit = | [5 empty] | 648 | kg/d
| TSSC of Grit = | [5 empty] | 26500 | g/m3
| Flow rate = | [5 empty] | 24.4528 | m3/d
| BODC of Grit | [5 empty] | 767.652 | g/m3
| BODM of grit = | [5 empty] | 18.7713 | kg/d
d. | TSSM after grit removal ( influent to primary settling tank)
| TSSM = | [5 empty] | 14210.7847 | kg/d | {(m3/d* g/m3) /(g/kg)}
2 | Estimate the concentration of soluble BODC in the effluent using the following relationship :
| Eflluent BODC = Influent solube BODC escaping treatment (S) + BODC of effluent TSS | [10 empty] | Equation (8-26), Pg-726
a. | Determining BODC of effluent TSS
| Biodegradability portion of TSS (VSS/TSS)= | [5 empty] | 65%
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| Ratio of BODC by Ultimate BODC (BOD/UBOD)= | [5 empty] | 0.68
| BODC of Effluent TSSC = | [5 empty] | 18.8292 | g/m3 | {(g/g)/( g/g) *(g/g)/( g/g) *(g/g)/( g/g) }*g/m3
Eflluent BODC = Influent solube BODC escaping treatment + BODC of effluent TSS
20=S+13.8
| S= | [5 empty] | 1.1708 | g/m3
a. | Primary Sedimentation
i. | Operating Parameters
| BOD removal= | [5 empty] | 33%
| TSS removal = | [5 empty] | 50%
ii. | BODM removed = | [5 empty] | 3491.6265 | kg/d
iii. | BODM to secondary = | [5 empty] | 7089.0598 | kg/d
iv. | TSSM removed = | [5 empty] | 7105.3923 | kg/d
v. | TSSM to secondary = | [5 empty] | 7105.3923 | kg/d
b. | Determine volatile fraction of primary sludge
i. | Operating Parameters
| Concentration of primary sludge = | [5 empty] | 4%
| Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67%
| Assume Volatile fraction of grit = | [5 empty] | 3%
| VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
| VSSM in influent prior to grit removal = | [5 empty] | 9955.3857 | kg/d
| VSSM removed in grit chamber = | [5 empty] | 19.44 | kg/d
| VSSM in secondary influent = | [5 empty] | 6039.5835 | kg/d
| VSSM in primary sludge = | [5 empty] | 3896.3622 | kg/d
| Flow Rate of Primary Sludge = | [5 empty] | 177.6348 | m3/d
| Volatile Fraction in Primary Sludge = | [5 empty] | 54.84%
c. | Gravity Thickening of Primary Sludge
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
| Specific Gravity of Solids = | [5 empty] | 1
i. | Determine Flowrate of the Thickened Sludge = | [5 empty] | 100.6597 | m3/d
ii. | Determine flowrate recycled to the plant influent = | [5 empty] | 76.9751 | m3/d
iii. | Determine TSSM to the digestor = | [5 empty] | 6039.5835 | kg/d
iv. | Determine TSSM recycled to the plant influent = | [5 empty] | 1065.8089 | kg/d
v. | TSSC of the recycled flow = | [5 empty] | 13846.1538 | g/m3
vi. | BODC of the TSSC of recycled flow= | [5 empty] | 7331.5816 | g/m3
vii. | BODM of the recyled flow = | [5 empty] | 564.3491 | kg/d
viii. | BODC of the TSSC of flow going to digestor= | [5 empty] | 31770.187 | g/m3
ix. | BODM of the digestor flow = | [5 empty] | 3197.9783 | kg/d
c. | Secondary Process
i. | Determining the secondary process operating parameters
| Flowrate = | [5 empty] | 32811.8883 | m3/d
| The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
| Aeration tank volume, Vr = | [5 empty] | 7900 | m3
| Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
| Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
| Solids Retention Time, SRT = | [5 empty] | 10 | d
| BODM to secondary = | [5 empty] | 7089.0598 | kg/d
| BODC to secondary (S0) = | [5 empty] | 216.0516 | g/m3 | {((kg/d)/(m3/d))/(kg/g)}
| Influent solube BODC escaping treatment (S) = | [5 empty] | 1.1708 | g/m3
| MLSS in Return Activated Sludge= | [5 empty] | 7000
| Mixed Liquor VSSC = | [5 empty] | 2789.0204 | g/m3 | Pg-600, Eq 7-42
| Mixed Liquor TSSC = | [5 empty] | 3486.2755 | g/m3
| Yobs = | [5 empty] | 0.3125 |  | Pg-603, Eq 7-59
ii. | Determine Effluent Mass Quantities
| BODM = | [5 empty] | 656.2378 | kg/d
| TSSM = | [5 empty] | 984.3566 | kg/d
iii. | Estimate Mass of Volatile solids produced in the activated sludge process that must be waste.
| PX,VSS = | [5 empty] | 2203.3261 | kg/d | Pg-720 Eq 8-19
iv. | Estimate the TSSM that must be wasted
| TSSM = | [5 empty] | 2754.1577 | kg/d
v. | Estimate the waste quantities discharged to the thicker. It is assumed that the wasting is from the secondary clarifier
| TSSM = | [5 empty] | 1769.801 | kg/d
| Flowrate = | [5 empty] | 252.8287 | m3/d
d. | Flotation Thickeners
i. | Operating Parameters
| Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
| ( specific gravity of the solids ) = | [5 empty] | 1
ii. | Determine flowrate of the thickened sludge
| Solid captured by thickener = | [5 empty] | 1592.8209 | kg/d
| Flowrate = | [5 empty] | 31.8564 | m3/d
iii. | Determine Flowrate recyled to the plant influent
| Recycled Flowrate = | [5 empty] | 220.9723 | m3/d
iv. | Determine the TSSM to the digester
| TSSM = | [5 empty] | 1592.8209 | kg/d
v | Determine the BODC of the TSSC going to digester
| TSSC = | [5 empty] | 50000 | g/m3
| BODC of the TSSC = | [5 empty] | 38624 | g/m3
| BODM = | [5 empty] | 1230.4223 | kg/d
vi | Determine the TSSM recyled to the plant influent
| TSSM = | [5 empty] | 176.9801 | kg/d
vii | Determine the BODC of the TSSC in the recyled flow
| TSSC in the recyled flow = | [5 empty] | 800.9153 | g/m3
| BODC of the TSSC = | [5 empty] | 502.6865 | g/m3 |  |  | Equation (8-26), Pg-726
| BODM = | [5 empty] | 111.0798 | kg/d
e. | Sludge Digestion
i. | Operating Parameters
| SRT = | [5 empty] | 20 | d
| Volatile Solids Reduction, VSR = | [5 empty] | 60%
| BODC in digester supernatant = | [5 empty] | 1000 | g/m3
| TSSC in digested sludge = | [5 empty] | 5%
ii. | Determine the solids fed to the digester and the corresponding flowrate.
TSSM = Solids fed from gravity thickener and solids fed from thickener
| TSSM = | [5 empty] | 7632.4044 | kg/d
| Total Flowrate = | [5 empty] | 132.5161 | m3/d
iii. | Determine the VSSM fed to the digester
| VSSM = | [5 empty] | 4586.1646 | kg/d
| Percentage VSSM in mixture = | [5 empty] | 60.09%
iv. | Determine the VSS destroyed
| VSSM = | [5 empty] | 2751.6988 | kg/d
v. | Determine the mass flowrate to the digester
| Mass Flow from Primary Sludge = | [5 empty] | 100659.7248 | kg/d |  | (Unitary method, if 6% has a mass of 5443.2 kg, how much does 100% have)
| Mass Flow from Thickened Activated Sludge = | [5 empty] | 31856.4183 | kg/d |  | (Unitary method, if 4% has a mass of 1433 kg, how much does 100% have)
Parameters for Digester
| Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized | [5 empty] | Pg,1506,1507, Eq 13-12, 13-13
| b = | [5 empty] | 0.03 | d-1
| S0= | [5 empty] | 4428.4006 | kg/d | (Combined BODC from Primary and Secondary Sludge)
| S= | [5 empty] | 1771.3602 | kg/d | BODC after digestion based on percentage reduction of VSS
| Q= | [5 empty] | 132.5161 | m3/d | Combined Flow rate
| SRT = | [5 empty] | 20 | d
| PX = | [5 empty] | 132.852 | kg/d | Net Mass of Cell tissue produced per day
| VCH4 = | [5 empty] | 863.9367 | m3/d
| VGAS = | [5 empty] | 1329.1333 | m3/d | (Assuming 65% of biogas as methane)
| Biogas Mass = | [5 empty] | 1488.6293 | kg/d | (Assuming density of biogas as 1.12 kg/m3)
vi. | Determine the mass quantities of gas and sludge after digestion.
Fixed Solids = TSSM - VSSM
| Fixed Solids = | [5 empty] | 3046.2398 | kg/d
| TSSM in digested sludge= | [5 empty] | 4880.7056 | kg/d
Mass Balance of Digested Output
| Mass IN = | [5 empty] | 132516.1431 | kg/d
| Gas Produced = | [5 empty] | 1488.6293 | kg/d
| Mass Out = | [5 empty] | 131027.5138 | kg/d | (Solids and Liquid)
vii. | Determine the flowrate distribution between the supernatant at 0.5% solids and digested Sludge at 5% solids. Let X = TSS of Supernatant
| TSSC of Supernatant = | [5 empty] | 0.5%
| TSSC of Digested Sludge = | [5 empty] | 5%
Mass Flow of Supernatant + Mass Flow of Digested Solids = Mass Out
Let X be TSSM of Supernatant
{(X/0.005)+((4443-X)/0.05)}=123729
Solve for X
| X = | [5 empty] | 185.63 | kg/d
| TSSM of Supernatant = | [5 empty] | 185.63 | kg/d
| TSSM of Digested Sludge = | [5 empty] | 4695.0756 | kg/d
| Supernatant Flowrate = | [5 empty] | 37.126 | m3/d
| Digested Sludge Flowrate = | [5 empty] | 93.9015 | m3/d
viii. | Establish the characteristics of the recycled flow
| Flowrate = | [5 empty] | 37.126 | m3/d
| BODM of Supernatant = | [5 empty] | 37.126 | kg/d
| TSSM of Supernatant = | [5 empty] | 185.63 | kg/d
f. | Sludge Dewatering
i. | Operating Parameters for centrifuge :
| Sludge cake = | [5 empty] | 22% | solids
| Specific gravity of sludge = | [5 empty] | 1.123
| Solids capture = | [5 empty] | 90%
| Centrate BODC = | [5 empty] | 2000 | mg/L
| Density of Water = | [5 empty] | 1000 | kg/m3
ii. | Determine the Sludge-cake characteristics.
| TSSM = | [5 empty] | 4225.568 | kg/d |  | 19207.1275
| Flow rate = | [5 empty] | 17.1034 | m3/d
| BODC of the TSSC = | [5 empty] | 155064.7384 | g/m3
| BODM of the TSSC = | [5 empty] | 2652.1355 | kg/d
iii. | Determine the Centrate Characteristics
| Flowrate = | [5 empty] | 76.7981 | m3/d
| BODM = | [5 empty] | 153.5962 | kg/d
| TSSM = | [5 empty] | 469.5076 | kg/d
g. | Prepare a summary table of the recycle flows and waste characteristics for the first iteration
Incremental change from previous iteration
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Gravity Thickener | 76.9751 | 564.3491 | 1065.8089 | 0 | 0 | 0
| Flotation Thickener | 220.9723 | 111.0798 | 176.9801 | -0.014853 | -0.0074665 | 0.2174
| Digester Supernatant | 37.126 | 37.126 | 185.63 | -0.0011111 | -0.0011111 | -0.0055557
| Centrate | 76.7981 | 153.5962 | 469.5076 | -0.0008198 | -0.0016396 | -0.0050118
| Totals | 411.8715 | 866.1511 | 1897.9265 | -0.016784 | -0.010217 | 0.20683
[5 empty] | -0.004075% | -0.00118% | 0.0109%
| Operation | Flowrate, m3/d | BODM , kg/d | TSSM , kg/d
| Raw Sewage | 32400 | 9720 | 12960
| Grit Removal | 24.4528 | 18.7713 | 648
| Primary Sedimentation Inlet | 32811.8883 | 10580.6862 | 14210.7847
| Primary Sludge | 177.6348 | 3491.6265 | 7105.3923
| Gravity Thickened Sludge | 100.6597 | 3197.9783 | 6039.5835
| Centrate | 76.9751 | 564.3491 | 1065.8089
| Aeration Tank Inlet | 32634.2535 | 7089.0598 | 7105.3923
| Secondary Clarifier Outlet | 32381.4247 | 656.2378 | 984.3566
| Effluent | 32381.4247 | 323.8142 | 323.8142
| Waste Activated Sludge | 252.8287 | 1341.5021 | 1769.801
| Flotation Thickener Sludge | 31.8564 | 1230.4223 | 1592.8209
| Centrate | 220.9723 | 111.0798 | 176.9801
| Inlet for AD | 132.5161 | 4428.4006 | 7632.4044
| Gas | 1488.6293 | kg/d
| Supernatant | 37.126 | 37.126 | 185.63
| Digestate | 93.9015 | 2805.7317 | 4695.0756
| Dewatered Disgestate | 17.1034 | 2652.1355 | 4225.568
| Centrate | 76.7981 | 153.5962 | 469.5076
| Return Flows | 411.8715 | 866.1511 | 1897.9265
Raw Sewage
Pre- Treatment Facility
Raw Sewage
Flow(m3/d) = 32400
TSS(kg/d) = 12960
BOD(kg/d) = 9720
Grit Removal
Flow(m3/d) = 24
TSS(kg/d) = 648
BOD(kg/d) = 19
Primary Settling Inlet
Flow(m3/d) = 32812
TSS(kg/d) = 14211
BOD(kg/d) = 10581
Primary
Settling
Aeration Tank
Aeration Tank Inlet
Flow(m3/d) = 32634
TSS(kg/d) = 7105
BOD(kg/d) = 7089
Secondary Clarifier
Tertiary
Treatment
Clarifier Outlet
Flow(m3/d) = 32381
TSS(kg/d) = 984
BOD(kg/d) = 656
Effluent
Flow(m3/d) = 32381
TSS(kg/d) = 324
BOD(kg/d) = 324
Treated Sewage
Gravity Thickener
Primary Sludge
Flow(m3/d) = 178
TSS(kg/d) = 7105
BOD(kg/d) = 3492
Flotation
Thickener
Blending Tank
Anaerobic Digestor
Biosolids Dewatering
Biogas
Biosolids
Waste Activated Sludge
Flow(m3/d) = 253
TSS(kg/d) = 1770
BOD(kg/d) = 1342
Return Flow
Flow(m3/d) = 412
TSS(kg/d) = 1898
BOD(kg/d) = 866
Thickener Overflow
Flow(m3/d) = 221
TSS(kg/d) = 177
BOD(kg/d) = 111
Thickened WAS
Flow(m3/d) = 32
TSS(kg/d) = 1806
BOD(kg/d) = 1369
Thickened Primary Sludge
Flow(m3/d) = 101
TSS(kg/d) = 6040
BOD(kg/d) = 3198
Thickener Overflow
Flow(m3/d) = 77
TSS(kg/d) = 1066
BOD(kg/d) = 564
Digestor Inlet
Flow(m3/d) = 134
TSS(kg/d) = 7632
BOD(kg/d) = 4428
Supernatant
Flow(m3/d) = 37
TSS(kg/d) = 186
BOD(kg/d) = 37
Digestate
Flow(m3/d) = 94
TSS(kg/d) = 4695
BOD(kg/d) = 2806
Centrate
Flow(m3/d) = 77
TSS(kg/d) = 470
BOD(kg/d) = 154 156
Biosolids
Flow(m3/d) = 17
TSS(kg/d) = 4226
BOD(kg/d) = 2652
Biogas
1489 kg/d
Raw Sewage
Pre- Treatment Facility
Flow(m3/d) = 32400
TSS(kg/d) = 12960
BOD(kg/d) = 9720
24
648
19
32812
14211
10581
Primary
Settling
Aeration Tank
32634
7105
7089
Secondary Clarifier
Tertiary
Treatment
Treated Sewage
Gravity Thickener
Flotation
Thickener
Blending Tank
Anaerobic Digestor
Biosolids Dewatering
Biogas
Biosolids
Biogas 1489 kg/d
32381
984
656
32381
324
324
253
1770
1342
32
1593
1230
94
4695
2806
77
154
470
37
186
37
133
7632
4428
101
6040
3198
77
1066
564
221
177
111
178
7105
3492
412
1898
866
17
4226
2652

## 5th Iteration
Preparation of a Solids Mass Balance for 32.4 MLD GWWTP in Kathmandu
1 | Definition of terms
BODC = biochemical oxygen demand expressed as a concentration, g/m3
BODM = biochemical oxygen demand expressed as a mass, kg/d
TSSC = total suspended solids expressed as a concentration, g/m3
TSSM = total suspended solids expressed as a mass, kg/d
2 | Wastewater flowrates
a. | Annual average flowrate | [5 empty] | 32400 | m3/d
b. | Return Flowrate | [5 empty] | 407.9824 | m3/d
c. | Total average flowrate = | [5 empty] | 32807.9824 | m3/d
3 | Influent characteristics | [10 empty] | Legend
a. | BODC = | [5 empty] | 300 | g/m3 |  |  |  |  | Real Values Taken From WWTP
b. | TSSC = | [5 empty] | 400 | g/m3 |  |  |  |  | Values taken from Metcalf & Eddy
c. | Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67% | [5 empty] | Computed Values
| TSS removed in grit = | [5 empty] | 5% | [5 empty] | Referenced Values
d. | TSSC after grit removal = | [5 empty] | 380 | g/m3
e. | Assume Volatile fraction of grit = | [5 empty] | 3%
| Specific Gravity of Grit = | [5 empty] | 2.65 | kg/m3
| Solids Concentration in Grit = | [5 empty] | 1%
4 | Sludge and biosolids characteristics
a. | Concentration of primary sludge = | [5 empty] | 4%
b. | Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
c. | (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
d. | Total suspended solids in digested sludge = | [5 empty] | 5%
e. | Special Gravity of Solids = | [5 empty] | 1
f. | Fraction of the biological solids that are biodegradable = | [5 empty] | 65%
g. | The value of BODC can be obtained by multiplying the value of UBOD by a factor of | [5 empty] | 0.68
5 | Effluent characteristics
a. | BODC = | [5 empty] | 10 | g/m3
b. | TSSC = | [5 empty] | 10 | g/m3
Secondary Clarifier Outlet characteristics
c. | BODC = | [5 empty] | 20 | g/m3
d. | TSSC = | [5 empty] | 30 | g/m3
6 | Primary clarifier
Assumtions,
a. | BOD removal= | [5 empty] | 33%
b. | TSS removal = | [5 empty] | 50%
c. | VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
7 | Secondary treatment
Assumption,
a. | The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
b. | Aeration tank volume, Vr = | [5 empty] | 7900 | m3
c. | Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
d. | Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
e. | Solids Retention Time, SRT = | [5 empty] | 10 | d
f. | MLSS in Return Activated Sludge= | [5 empty] | 7000 | g/m3
8 | Sludge digestion
Assumption,
a. | SRT = | [5 empty] | 20 | d
b. | Volatile Solids Reduction, VSR = | [5 empty] | 60%
d. | BODC in digester supernatant = | [5 empty] | 1000 | g/m3
e. | TSSC in digested sludge = | [5 empty] | 5%
f. | Yield Coefficient, Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized
g. | Endogenous coefficient, b = | [5 empty] | 0.03 | d-1
9 | Sludge dewatering
Assumptions,
a. | Sludge cake = | [5 empty] | 22% | solids
b. | Specific gravity of sludge = | [5 empty] | 1.123
c. | Solids capture = | [5 empty] | 90%
d. | Centrate BODC = | [5 empty] | 2000 | mg/L
10 | Other Important Values
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| TSSC of Supernatant = | [5 empty] | 0.5%
| Density of Water = | [5 empty] | 1000 | kg/m3
SOLUTION
1 | Convert the given constitient quantities to daily mass values
a. | BODM in influent :
| BODM = | [5 empty] | 9720 | kg/d | {(m3/d* g/m3) /(g/kg)}
| BODM of return flow = | [5 empty] | 879.4575 | kg/d
| BODM total = | [5 empty] | 10599.4575 | kg/d
b | TSSM in influent
| TSSM = | [5 empty] | 12960 | kg/d | {(m3/d* g/m3) /(g/kg)}
| TSSM of return flow = | [5 empty] | 1898.7847 | kg/d
| TSSM of combined flow = | [5 empty] | 14858.7847 | kg/d
c. | TSSM removed in grit = | [5 empty] | 648 | kg/d
| TSSC of Grit = | [5 empty] | 26500 | g/m3
| Flow rate = | [5 empty] | 24.4528 | m3/d
| BODC of Grit | [5 empty] | 767.652 | g/m3
| BODM of grit = | [5 empty] | 18.7713 | kg/d
d. | TSSM after grit removal ( influent to primary settling tank)
| TSSM = | [5 empty] | 14210.7847 | kg/d | {(m3/d* g/m3) /(g/kg)}
2 | Estimate the concentration of soluble BODC in the effluent using the following relationship :
| Eflluent BODC = Influent solube BODC escaping treatment (S) + BODC of effluent TSS | [10 empty] | Equation (8-26), Pg-726
a. | Determining BODC of effluent TSS
| Biodegradability portion of TSS (VSS/TSS)= | [5 empty] | 65%
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| Ratio of BODC by Ultimate BODC (BOD/UBOD)= | [5 empty] | 0.68
| BODC of Effluent TSSC = | [5 empty] | 18.8292 | g/m3 | {(g/g)/( g/g) *(g/g)/( g/g) *(g/g)/( g/g) }*g/m3
Eflluent BODC = Influent solube BODC escaping treatment + BODC of effluent TSS
20=S+13.8
| S= | [5 empty] | 1.1708 | g/m3
a. | Primary Sedimentation
i. | Operating Parameters
| BOD removal= | [5 empty] | 33%
| TSS removal = | [5 empty] | 50%
ii. | BODM removed = | [5 empty] | 3491.6265 | kg/d
iii. | BODM to secondary = | [5 empty] | 7089.0598 | kg/d
iv. | TSSM removed = | [5 empty] | 7105.3923 | kg/d
v. | TSSM to secondary = | [5 empty] | 7105.3923 | kg/d
b. | Determine volatile fraction of primary sludge
i. | Operating Parameters
| Concentration of primary sludge = | [5 empty] | 4%
| Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67%
| Assume Volatile fraction of grit = | [5 empty] | 3%
| VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
| VSSM in influent prior to grit removal = | [5 empty] | 9955.3857 | kg/d
| VSSM removed in grit chamber = | [5 empty] | 19.44 | kg/d
| VSSM in secondary influent = | [5 empty] | 6039.5835 | kg/d
| VSSM in primary sludge = | [5 empty] | 3896.3622 | kg/d
| Flow Rate of Primary Sludge = | [5 empty] | 177.6348 | m3/d
| Volatile Fraction in Primary Sludge = | [5 empty] | 54.84%
c. | Gravity Thickening of Primary Sludge
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
| Specific Gravity of Solids = | [5 empty] | 1
i. | Determine Flowrate of the Thickened Sludge = | [5 empty] | 100.6597 | m3/d
ii. | Determine flowrate recycled to the plant influent = | [5 empty] | 76.9751 | m3/d
iii. | Determine TSSM to the digestor = | [5 empty] | 6039.5835 | kg/d
iv. | Determine TSSM recycled to the plant influent = | [5 empty] | 1065.8089 | kg/d
v. | TSSC of the recycled flow = | [5 empty] | 13846.1538 | g/m3
vi. | BODC of the TSSC of recycled flow= | [5 empty] | 7331.5816 | g/m3
vii. | BODM of the recyled flow = | [5 empty] | 564.3491 | kg/d
viii. | BODC of the TSSC of flow going to digestor= | [5 empty] | 31770.187 | g/m3
ix. | BODM of the digestor flow = | [5 empty] | 3197.9783 | kg/d
c. | Secondary Process
i. | Determining the secondary process operating parameters
| Flowrate = | [5 empty] | 32807.9824 | m3/d
| The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
| Aeration tank volume, Vr = | [5 empty] | 7900 | m3
| Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
| Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
| Solids Retention Time, SRT = | [5 empty] | 10 | d
| BODM to secondary = | [5 empty] | 7089.0598 | kg/d
| BODC to secondary (S0) = | [5 empty] | 216.0773 | g/m3 | {((kg/d)/(m3/d))/(kg/g)}
| Influent solube BODC escaping treatment (S) = | [5 empty] | 1.1708 | g/m3
| MLSS in Return Activated Sludge= | [5 empty] | 7000
| Mixed Liquor VSSC = | [5 empty] | 2789.0222 | g/m3 | Pg-600, Eq 7-42
| Mixed Liquor TSSC = | [5 empty] | 3486.2778 | g/m3
| Yobs = | [5 empty] | 0.3125 |  | Pg-603, Eq 7-59
ii. | Determine Effluent Mass Quantities
| BODM = | [5 empty] | 656.1596 | kg/d
| TSSM = | [5 empty] | 984.2395 | kg/d
iii. | Estimate Mass of Volatile solids produced in the activated sludge process that must be waste.
| PX,VSS = | [5 empty] | 2203.3276 | kg/d | Pg-720 Eq 8-19
iv. | Estimate the TSSM that must be wasted
| TSSM = | [5 empty] | 2754.1594 | kg/d
v. | Estimate the waste quantities discharged to the thicker. It is assumed that the wasting is from the secondary clarifier
| TSSM = | [5 empty] | 1769.92 | kg/d
| Flowrate = | [5 empty] | 252.8457 | m3/d
d. | Flotation Thickeners
i. | Operating Parameters
| Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
| ( specific gravity of the solids ) = | [5 empty] | 1
ii. | Determine flowrate of the thickened sludge
| Solid captured by thickener = | [5 empty] | 1592.928 | kg/d
| Flowrate = | [5 empty] | 31.8586 | m3/d
iii. | Determine Flowrate recyled to the plant influent
| Recycled Flowrate = | [5 empty] | 220.9872 | m3/d
iv. | Determine the TSSM to the digester
| TSSM = | [5 empty] | 1592.928 | kg/d
v | Determine the BODC of the TSSC going to digester
| TSSC = | [5 empty] | 50000 | g/m3
| BODC of the TSSC = | [5 empty] | 38624 | g/m3
| BODM = | [5 empty] | 1230.505 | kg/d
vi | Determine the TSSM recyled to the plant influent
| TSSM = | [5 empty] | 176.992 | kg/d
vii | Determine the BODC of the TSSC in the recyled flow
| TSSC in the recyled flow = | [5 empty] | 800.9153 | g/m3
| BODC of the TSSC = | [5 empty] | 502.6865 | g/m3 |  |  | Equation (8-26), Pg-726
| BODM = | [5 empty] | 111.0873 | kg/d
e. | Sludge Digestion
i. | Operating Parameters
| SRT = | [5 empty] | 20 | d
| Volatile Solids Reduction, VSR = | [5 empty] | 60%
| BODC in digester supernatant = | [5 empty] | 1000 | g/m3
| TSSC in digested sludge = | [5 empty] | 5%
ii. | Determine the solids fed to the digester and the corresponding flowrate.
TSSM = Solids fed from gravity thickener and solids fed from thickener
| TSSM = | [5 empty] | 7632.5115 | kg/d
| Total Flowrate = | [5 empty] | 132.5183 | m3/d
iii. | Determine the VSSM fed to the digester
| VSSM = | [5 empty] | 4586.2503 | kg/d
| Percentage VSSM in mixture = | [5 empty] | 60.09%
iv. | Determine the VSS destroyed
| VSSM = | [5 empty] | 2751.7502 | kg/d
v. | Determine the mass flowrate to the digester
| Mass Flow from Primary Sludge = | [5 empty] | 100659.7248 | kg/d |  | (Unitary method, if 6% has a mass of 5443.2 kg, how much does 100% have)
| Mass Flow from Thickened Activated Sludge = | [5 empty] | 31858.5596 | kg/d |  | (Unitary method, if 4% has a mass of 1433 kg, how much does 100% have)
Parameters for Digester
| Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized | [5 empty] | Pg,1506,1507, Eq 13-12, 13-13
| b = | [5 empty] | 0.03 | d-1
| S0= | [5 empty] | 4428.4833 | kg/d | (Combined BODC from Primary and Secondary Sludge)
| S= | [5 empty] | 1771.3933 | kg/d | BODC after digestion based on percentage reduction of VSS
| Q= | [5 empty] | 132.5183 | m3/d | Combined Flow rate
| SRT = | [5 empty] | 20 | d
| PX = | [5 empty] | 132.8545 | kg/d | Net Mass of Cell tissue produced per day
| VCH4 = | [5 empty] | 863.9528 | m3/d
| VGAS = | [5 empty] | 1329.1582 | m3/d | (Assuming 65% of biogas as methane)
| Biogas Mass = | [5 empty] | 1488.6571 | kg/d | (Assuming density of biogas as 1.12 kg/m3)
vi. | Determine the mass quantities of gas and sludge after digestion.
Fixed Solids = TSSM - VSSM
| Fixed Solids = | [5 empty] | 3046.2612 | kg/d
| TSSM in digested sludge= | [5 empty] | 4880.7613 | kg/d
Mass Balance of Digested Output
| Mass IN = | [5 empty] | 132518.2844 | kg/d
| Gas Produced = | [5 empty] | 1488.6571 | kg/d
| Mass Out = | [5 empty] | 131029.6273 | kg/d | (Solids and Liquid)
vii. | Determine the flowrate distribution between the supernatant at 0.5% solids and digested Sludge at 5% solids. Let X = TSS of Supernatant
| TSSC of Supernatant = | [5 empty] | 0.5%
| TSSC of Digested Sludge = | [5 empty] | 5%
Mass Flow of Supernatant + Mass Flow of Digested Solids = Mass Out
Let X be TSSM of Supernatant
{(X/0.005)+((4443-X)/0.05)}=123729
Solve for X
| X = | [5 empty] | 185.6356 | kg/d
| TSSM of Supernatant = | [5 empty] | 185.6356 | kg/d
| TSSM of Digested Sludge = | [5 empty] | 4695.1257 | kg/d
| Supernatant Flowrate = | [5 empty] | 37.1271 | m3/d
| Digested Sludge Flowrate = | [5 empty] | 93.9025 | m3/d
viii. | Establish the characteristics of the recycled flow
| Flowrate = | [5 empty] | 37.1271 | m3/d
| BODM of Supernatant = | [5 empty] | 37.1271 | kg/d
| TSSM of Supernatant = | [5 empty] | 185.6356 | kg/d
f. | Sludge Dewatering
i. | Operating Parameters for centrifuge :
| Sludge cake = | [5 empty] | 22% | solids
| Specific gravity of sludge = | [5 empty] | 1.123
| Solids capture = | [5 empty] | 90%
| Centrate BODC = | [5 empty] | 2000 | mg/L
| Density of Water = | [5 empty] | 1000 | kg/m3
ii. | Determine the Sludge-cake characteristics.
| TSSM = | [5 empty] | 4225.6132 | kg/d |  | 19207.3325
| Flow rate = | [5 empty] | 17.1036 | m3/d
| BODC of the TSSC = | [5 empty] | 155064.7384 | g/m3
| BODM of the TSSC = | [5 empty] | 2652.1638 | kg/d
iii. | Determine the Centrate Characteristics
| Flowrate = | [5 empty] | 76.7989 | m3/d
| BODM = | [5 empty] | 153.5978 | kg/d
| TSSM = | [5 empty] | 469.5126 | kg/d
g. | Prepare a summary table of the recycle flows and waste characteristics for the first iteration
Incremental change from previous iteration
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Gravity Thickener | 76.9751 | 564.3491 | 1065.8089 | -0.062428 | -0.40898 | -0.86439
| Flotation Thickener | 220.9872 | 111.0873 | 176.992 | 0.28629 | 0.14391 | 0.22929
| Digester Supernatant | 37.1271 | 37.1271 | 185.6356 | 20.3951 | 20.3951 | 101.9754
| Centrate | 76.7989 | 153.5978 | 469.5126 | -16.7131 | -33.4262 | -102.176
| Totals | 411.8883 | 866.1613 | 1897.949 | 3.9059 | -13.2962 | -0.83569
[5 empty] | 0.9483% | -1.535% | -0.04403%
| Operation | Flowrate, m3/d | BODM , kg/d | TSSM , kg/d
| Raw Sewage | 32400 | 9720 | 12960
| Grit Removal | 24.4528 | 18.7713 | 648
| Primary Sedimentation Inlet | 32807.9824 | 10580.6862 | 14210.7847
| Primary Sludge | 177.6348 | 3491.6265 | 7105.3923
| Gravity Thickened Sludge | 100.6597 | 3197.9783 | 6039.5835
| Centrate | 76.9751 | 564.3491 | 1065.8089
| Aeration Tank Inlet | 32630.3476 | 7089.0598 | 7105.3923
| Secondary Clarifier Outlet | 32377.5019 | 656.1596 | 984.2395
| Effluent | 32377.5019 | 323.775 | 323.775
| Waste Activated Sludge | 252.8457 | 1341.5923 | 1769.92
| Flotation Thickener Sludge | 31.8586 | 1230.505 | 1592.928
| Centrate | 220.9872 | 111.0873 | 176.992
| Inlet for AD | 132.5183 | 4428.4833 | 7632.5115
| Gas | 1488.6571 | kg/d
| Supernatant | 37.1271 | 37.1271 | 185.6356
| Digestate | 93.9025 | 2805.7617 | 4695.1257
| Dewatered Disgestate | 17.1036 | 2652.1638 | 4225.6132
| Centrate | 76.7989 | 153.5978 | 469.5126
| Return Flows | 411.8883 | 866.1613 | 1897.949

## 4th Iteration
Preparation of a Solids Mass Balance for 32.4 MLD GWWTP in Kathmandu
1 | Definition of terms
BODC = biochemical oxygen demand expressed as a concentration, g/m3
BODM = biochemical oxygen demand expressed as a mass, kg/d
TSSC = total suspended solids expressed as a concentration, g/m3
TSSM = total suspended solids expressed as a mass, kg/d
2 | Wastewater flowrates
a. | Annual average flowrate | [5 empty] | 32400 | m3/d
b. | Return Flowrate | [5 empty] | 414.0414 | m3/d
c. | Total average flowrate = | [5 empty] | 32814.0414 | m3/d
3 | Influent characteristics | [10 empty] | Legend
a. | BODC = | [5 empty] | 300 | g/m3 |  |  |  |  | Real Values Taken From WWTP
b. | TSSC = | [5 empty] | 400 | g/m3 |  |  |  |  | Values taken from Metcalf & Eddy
c. | Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67% | [5 empty] | Computed Values
| TSS removed in grit = | [5 empty] | 5% | [5 empty] | Referenced Values
d. | TSSC after grit removal = | [5 empty] | 380 | g/m3
e. | Assume Volatile fraction of grit = | [5 empty] | 3%
| Specific Gravity of Grit = | [5 empty] | 2.65 | kg/m3
| Solids Concentration in Grit = | [5 empty] | 1%
4 | Sludge and biosolids characteristics
a. | Concentration of primary sludge = | [5 empty] | 4%
b. | Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
c. | (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
d. | Total suspended solids in digested sludge = | [5 empty] | 5%
e. | Special Gravity of Solids = | [5 empty] | 1
f. | Fraction of the biological solids that are biodegradable = | [5 empty] | 65%
g. | The value of BODC can be obtained by multiplying the value of UBOD by a factor of | [5 empty] | 0.68
5 | Effluent characteristics
a. | BODC = | [5 empty] | 10 | g/m3
b. | TSSC = | [5 empty] | 10 | g/m3
Secondary Clarifier Outlet characteristics
c. | BODC = | [5 empty] | 20 | g/m3
d. | TSSC = | [5 empty] | 30 | g/m3
6 | Primary clarifier
Assumtions,
a. | BOD removal= | [5 empty] | 33%
b. | TSS removal = | [5 empty] | 50%
c. | VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
7 | Secondary treatment
Assumption,
a. | The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
b. | Aeration tank volume, Vr = | [5 empty] | 7900 | m3
c. | Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
d. | Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
e. | Solids Retention Time, SRT = | [5 empty] | 10 | d
f. | MLSS in Return Activated Sludge= | [5 empty] | 7000 | g/m3
8 | Sludge digestion
Assumption,
a. | SRT = | [5 empty] | 20 | d
b. | Volatile Solids Reduction, VSR = | [5 empty] | 60%
d. | BODC in digester supernatant = | [5 empty] | 1000 | g/m3
e. | TSSC in digested sludge = | [5 empty] | 5%
f. | Yield Coefficient, Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized
g. | Endogenous coefficient, b = | [5 empty] | 0.03 | d-1
9 | Sludge dewatering
Assumptions,
a. | Sludge cake = | [5 empty] | 22% | solids
b. | Specific gravity of sludge = | [5 empty] | 1.123
c. | Solids capture = | [5 empty] | 90%
d. | Centrate BODC = | [5 empty] | 2000 | mg/L
10 | Other Important Values
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| TSSC of Supernatant = | [5 empty] | 0.5%
| Density of Water = | [5 empty] | 1000 | kg/m3
SOLUTION
1 | Convert the given constitient quantities to daily mass values
a. | BODM in influent :
| BODM = | [5 empty] | 9720 | kg/d | {(m3/d* g/m3) /(g/kg)}
| BODM of return flow = | [5 empty] | 871.4015 | kg/d
| BODM total = | [5 empty] | 10591.4015 | kg/d
b | TSSM in influent
| TSSM = | [5 empty] | 12960 | kg/d | {(m3/d* g/m3) /(g/kg)}
| TSSM of return flow = | [5 empty] | 1910.3098 | kg/d
| TSSM of combined flow = | [5 empty] | 14870.3098 | kg/d
c. | TSSM removed in grit = | [5 empty] | 648 | kg/d
| TSSC of Grit = | [5 empty] | 26500 | g/m3
| Flow rate = | [5 empty] | 24.4528 | m3/d
| BODC of Grit | [5 empty] | 767.652 | g/m3
| BODM of grit = | [5 empty] | 18.7713 | kg/d
d. | TSSM after grit removal ( influent to primary settling tank)
| TSSM = | [5 empty] | 14222.3098 | kg/d | {(m3/d* g/m3) /(g/kg)}
2 | Estimate the concentration of soluble BODC in the effluent using the following relationship :
| Eflluent BODC = Influent solube BODC escaping treatment (S) + BODC of effluent TSS | [10 empty] | Equation (8-26), Pg-726
a. | Determining BODC of effluent TSS
| Biodegradability portion of TSS (VSS/TSS)= | [5 empty] | 65%
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| Ratio of BODC by Ultimate BODC (BOD/UBOD)= | [5 empty] | 0.68
| BODC of Effluent TSSC = | [5 empty] | 18.8292 | g/m3 | {(g/g)/( g/g) *(g/g)/( g/g) *(g/g)/( g/g) }*g/m3
Eflluent BODC = Influent solube BODC escaping treatment + BODC of effluent TSS
20=S+13.8
| S= | [5 empty] | 1.1708 | g/m3
a. | Primary Sedimentation
i. | Operating Parameters
| BOD removal= | [5 empty] | 33%
| TSS removal = | [5 empty] | 50%
ii. | BODM removed = | [5 empty] | 3488.968 | kg/d
iii. | BODM to secondary = | [5 empty] | 7083.6623 | kg/d
iv. | TSSM removed = | [5 empty] | 7111.1549 | kg/d
v. | TSSM to secondary = | [5 empty] | 7111.1549 | kg/d
b. | Determine volatile fraction of primary sludge
i. | Operating Parameters
| Concentration of primary sludge = | [5 empty] | 4%
| Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67%
| Assume Volatile fraction of grit = | [5 empty] | 3%
| VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
| VSSM in influent prior to grit removal = | [5 empty] | 9963.1076 | kg/d
| VSSM removed in grit chamber = | [5 empty] | 19.44 | kg/d
| VSSM in secondary influent = | [5 empty] | 6044.4817 | kg/d
| VSSM in primary sludge = | [5 empty] | 3899.1859 | kg/d
| Flow Rate of Primary Sludge = | [5 empty] | 177.7789 | m3/d
| Volatile Fraction in Primary Sludge = | [5 empty] | 54.83%
c. | Gravity Thickening of Primary Sludge
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
| Specific Gravity of Solids = | [5 empty] | 1
i. | Determine Flowrate of the Thickened Sludge = | [5 empty] | 100.7414 | m3/d
ii. | Determine flowrate recycled to the plant influent = | [5 empty] | 77.0375 | m3/d
iii. | Determine TSSM to the digestor = | [5 empty] | 6044.4817 | kg/d
iv. | Determine TSSM recycled to the plant influent = | [5 empty] | 1066.6732 | kg/d
v. | TSSC of the recycled flow = | [5 empty] | 13846.1538 | g/m3
vi. | BODC of the TSSC of recycled flow= | [5 empty] | 7330.9492 | g/m3
vii. | BODM of the recyled flow = | [5 empty] | 564.7581 | kg/d
viii. | BODC of the TSSC of flow going to digestor= | [5 empty] | 31767.4467 | g/m3
ix. | BODM of the digestor flow = | [5 empty] | 3200.2958 | kg/d
c. | Secondary Process
i. | Determining the secondary process operating parameters
| Flowrate = | [5 empty] | 32814.0414 | m3/d
| The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
| Aeration tank volume, Vr = | [5 empty] | 7900 | m3
| Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
| Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
| Solids Retention Time, SRT = | [5 empty] | 10 | d
| BODM to secondary = | [5 empty] | 7083.6623 | kg/d
| BODC to secondary (S0) = | [5 empty] | 215.8729 | g/m3 | {((kg/d)/(m3/d))/(kg/g)}
| Influent solube BODC escaping treatment (S) = | [5 empty] | 1.1708 | g/m3
| MLSS in Return Activated Sludge= | [5 empty] | 7000
| Mixed Liquor VSSC = | [5 empty] | 2786.8843 | g/m3 | Pg-600, Eq 7-42
| Mixed Liquor TSSC = | [5 empty] | 3483.6054 | g/m3
| Yobs = | [5 empty] | 0.3125 |  | Pg-603, Eq 7-59
ii. | Determine Effluent Mass Quantities
| BODM = | [5 empty] | 656.2808 | kg/d
| TSSM = | [5 empty] | 984.4212 | kg/d
iii. | Estimate Mass of Volatile solids produced in the activated sludge process that must be waste.
| PX,VSS = | [5 empty] | 2201.6386 | kg/d | Pg-720 Eq 8-19
iv. | Estimate the TSSM that must be wasted
| TSSM = | [5 empty] | 2752.0483 | kg/d
v. | Estimate the waste quantities discharged to the thicker. It is assumed that the wasting is from the secondary clarifier
| TSSM = | [5 empty] | 1767.627 | kg/d
| Flowrate = | [5 empty] | 252.5181 | m3/d
d. | Flotation Thickeners
i. | Operating Parameters
| Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
| ( specific gravity of the solids ) = | [5 empty] | 1
ii. | Determine flowrate of the thickened sludge
| Solid captured by thickener = | [5 empty] | 1590.8643 | kg/d
| Flowrate = | [5 empty] | 31.8173 | m3/d
iii. | Determine Flowrate recyled to the plant influent
| Recycled Flowrate = | [5 empty] | 220.7009 | m3/d
iv. | Determine the TSSM to the digester
| TSSM = | [5 empty] | 1590.8643 | kg/d
v | Determine the BODC of the TSSC going to digester
| TSSC = | [5 empty] | 50000 | g/m3
| BODC of the TSSC = | [5 empty] | 38624 | g/m3
| BODM = | [5 empty] | 1228.9109 | kg/d
vi | Determine the TSSM recyled to the plant influent
| TSSM = | [5 empty] | 176.7627 | kg/d
vii | Determine the BODC of the TSSC in the recyled flow
| TSSC in the recyled flow = | [5 empty] | 800.9153 | g/m3
| BODC of the TSSC = | [5 empty] | 502.6865 | g/m3 |  |  | Equation (8-26), Pg-726
| BODM = | [5 empty] | 110.9433 | kg/d
e. | Sludge Digestion
i. | Operating Parameters
| SRT = | [5 empty] | 20 | d
| Volatile Solids Reduction, VSR = | [5 empty] | 60%
| BODC in digester supernatant = | [5 empty] | 1000 | g/m3
| TSSC in digested sludge = | [5 empty] | 5%
ii. | Determine the solids fed to the digester and the corresponding flowrate.
TSSM = Solids fed from gravity thickener and solids fed from thickener
| TSSM = | [5 empty] | 7635.346 | kg/d
| Total Flowrate = | [5 empty] | 132.5586 | m3/d
iii. | Determine the VSSM fed to the digester
| VSSM = | [5 empty] | 4586.9995 | kg/d
| Percentage VSSM in mixture = | [5 empty] | 60.08%
iv. | Determine the VSS destroyed
| VSSM = | [5 empty] | 1834.7998 | kg/d
v. | Determine the mass flowrate to the digester
| Mass Flow from Primary Sludge = | [5 empty] | 100741.3613 | kg/d |  | (Unitary method, if 6% has a mass of 5443.2 kg, how much does 100% have)
| Mass Flow from Thickened Activated Sludge = | [5 empty] | 31817.2867 | kg/d |  | (Unitary method, if 4% has a mass of 1433 kg, how much does 100% have)
Parameters for Digester
| Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized | [5 empty] | Pg,1506,1507, Eq 13-12, 13-13
| b = | [5 empty] | 0.03 | d-1
| S0= | [5 empty] | 4429.2067 | kg/d | (Combined BODC from Primary and Secondary Sludge)
| S= | [5 empty] | 1771.6827 | kg/d | BODC after digestion based on percentage reduction of VSS
| Q= | [5 empty] | 132.5586 | m3/d | Combined Flow rate
| SRT = | [5 empty] | 20 | d
| PX = | [5 empty] | 132.8762 | kg/d | Net Mass of Cell tissue produced per day
| VCH4 = | [5 empty] | 864.0939 | m3/d
| VGAS = | [5 empty] | 1329.3753 | m3/d | (Assuming 65% of biogas as methane)
| Biogas Mass = | [5 empty] | 1488.9003 | kg/d | (Assuming density of biogas as 1.12 kg/m3)
vi. | Determine the mass quantities of gas and sludge after digestion.
Fixed Solids = TSSM - VSSM
| Fixed Solids = | [5 empty] | 3048.3465 | kg/d
| TSSM in digested sludge= | [5 empty] | 5800.5462 | kg/d
Mass Balance of Digested Output
| Mass IN = | [5 empty] | 132558.648 | kg/d
| Gas Produced = | [5 empty] | 1488.9003 | kg/d
| Mass Out = | [5 empty] | 131069.7477 | kg/d | (Solids and Liquid)
vii. | Determine the flowrate distribution between the supernatant at 0.5% solids and digested Sludge at 5% solids. Let X = TSS of Supernatant
| TSSC of Supernatant = | [5 empty] | 0.5%
| TSSC of Digested Sludge = | [5 empty] | 5%
Mass Flow of Supernatant + Mass Flow of Digested Solids = Mass Out
Let X be TSSM of Supernatant
{(X/0.005)+((4443-X)/0.05)}=123729
Solve for X
| X = | [5 empty] | 83.6601 | kg/d
| TSSM of Supernatant = | [5 empty] | 83.6601 | kg/d
| TSSM of Digested Sludge = | [5 empty] | 5716.8861 | kg/d
| Supernatant Flowrate = | [5 empty] | 16.732 | m3/d
| Digested Sludge Flowrate = | [5 empty] | 114.3377 | m3/d
viii. | Establish the characteristics of the recycled flow
| Flowrate = | [5 empty] | 16.732 | m3/d
| BODM of Supernatant = | [5 empty] | 16.732 | kg/d
| TSSM of Supernatant = | [5 empty] | 83.6601 | kg/d
f. | Sludge Dewatering
i. | Operating Parameters for centrifuge :
| Sludge cake = | [5 empty] | 22% | solids
| Specific gravity of sludge = | [5 empty] | 1.123
| Solids capture = | [5 empty] | 90%
| Centrate BODC = | [5 empty] | 2000 | mg/L
| Density of Water = | [5 empty] | 1000 | kg/m3
ii. | Determine the Sludge-cake characteristics.
| TSSM = | [5 empty] | 5145.1975 | kg/d
| Flow rate = | [5 empty] | 20.8257 | m3/d
| BODC of the TSSC = | [5 empty] | 155064.7384 | g/m3
| BODM of the TSSC = | [5 empty] | 3229.3317 | kg/d
iii. | Determine the Centrate Characteristics
| Flowrate = | [5 empty] | 93.512 | m3/d
| BODM = | [5 empty] | 187.024 | kg/d
| TSSM = | [5 empty] | 571.6886 | kg/d
g. | Prepare a summary table of the recycle flows and waste characteristics for the first iteration
Incremental change from previous iteration
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Gravity Thickener | 77.0375 | 564.7581 | 1066.6732 | -0.47876 | -3.1365 | -6.629
| Flotation Thickener | 220.7009 | 110.9433 | 176.7627 | -1.1873 | -0.59684 | -0.95092
| Digester Supernatant | 16.732 | 16.732 | 83.6601 | -20.5751 | -20.5751 | -102.8757
| Centrate | 93.512 | 187.024 | 571.6886 | 16.1822 | 32.3644 | 98.9305
| Totals | 407.9824 | 879.4575 | 1898.7847 | -6.059 | 8.056 | -11.5252
[5 empty] | -1.485% | 0.916% | -0.607%
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Raw Sewage | 32400 | 9720 | 12960
| Grit Removal | 24.4528 | 18.7713 | 648
| Primary Sedimentation Inlet | 32814.0414 | 10572.6303 | 14222.3098
| Primary Sludge | 177.7789 | 3488.968 | 7111.1549
| Gravity Thickened Sludge | 100.7414 | 3200.2958 | 6044.4817
| Centrate | 77.0375 | 564.7581 | 1066.6732
| Aeration Tank Inlet | 32636.2625 | 7083.6623 | 7111.1549
| Secondary Clarifier Outlet | 32383.7444 | 656.2808 | 984.4212
| Effluent | 32383.7444 | 323.8374 | 323.8374
| Waste Activated Sludge | 252.5181 | 1339.8542 | 1767.627
| Flotation Thickener Sludge | 31.8173 | 1228.9109 | 1590.8643
| Centrate | 220.7009 | 110.9433 | 176.7627
| Inlet for AD | 132.5586 | 4429.2067 | 7635.346
| Gas | 1488.9003 | kg/d
| Supernatant | 16.732 | 16.732 | 83.6601
| Digestate | 114.3377 | 3416.3558 | 5716.8861
| Dewatered Disgestate | 20.8257 | 3229.3317 | 5145.1975
| Centrate | 93.512 | 187.024 | 571.6886
| Return Flows | 407.9824 | 879.4575 | 1898.7847

## 3rd Iteration
Preparation of a Solids Mass Balance for 32.4 MLD GWWTP in Kathmandu
1 | Definition of terms
BODC = biochemical oxygen demand expressed as a concentration, g/m3
BODM = biochemical oxygen demand expressed as a mass, kg/d
TSSC = total suspended solids expressed as a concentration, g/m3
TSSM = total suspended solids expressed as a mass, kg/d
2 | Wastewater flowrates
a. | Annual average flowrate | [5 empty] | 32400 | m3/d
b. | Return Flowrate | [5 empty] | 418.946 | m3/d
c. | Total average flowrate = | [5 empty] | 32818.946 | m3/d
3 | Influent characteristics | [10 empty] | Legend
a. | BODC = | [5 empty] | 300 | g/m3 |  |  |  |  | Real Values Taken From WWTP
b. | TSSC = | [5 empty] | 400 | g/m3 |  |  |  |  | Values taken from Metcalf & Eddy
c. | Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67% | [5 empty] | Computed Values
| TSS removed in grit = | [5 empty] | 5% | [5 empty] | Referenced Values
d. | TSSC after grit removal = | [5 empty] | 380 | g/m3
e. | Assume Volatile fraction of grit = | [5 empty] | 3%
| Specific Gravity of Grit = | [5 empty] | 2.65 | kg/m3
| Solids Concentration in Grit = | [5 empty] | 1%
4 | Sludge and biosolids characteristics
a. | Concentration of primary sludge = | [5 empty] | 4%
b. | Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
c. | (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
d. | Total suspended solids in digested sludge = | [5 empty] | 5%
e. | Special Gravity of Solids = | [5 empty] | 1
f. | Fraction of the biological solids that are biodegradable = | [5 empty] | 65%
g. | The value of BODC can be obtained by multiplying the value of UBOD by a factor of | [5 empty] | 0.68
5 | Effluent characteristics
a. | BODC = | [5 empty] | 10 | g/m3
b. | TSSC = | [5 empty] | 10 | g/m3
Secondary Clarifier Outlet characteristics
c. | BODC = | [5 empty] | 20 | g/m3
d. | TSSC = | [5 empty] | 30 | g/m3
6 | Primary clarifier
Assumtions,
a. | BOD removal= | [5 empty] | 33%
b. | TSS removal = | [5 empty] | 50%
c. | VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
7 | Secondary treatment
Assumption,
a. | The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
b. | Aeration tank volume, Vr = | [5 empty] | 7900 | m3
c. | Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
d. | Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
e. | Solids Retention Time, SRT = | [5 empty] | 10 | d
f. | MLSS in Return Activated Sludge= | [5 empty] | 7000 | g/m3
8 | Sludge digestion
Assumption,
a. | SRT = | [5 empty] | 20 | d
b. | Volatile Solids Reduction, VSR = | [5 empty] | 60%
d. | BODC in digester supernatant = | [5 empty] | 1000 | g/m3
e. | TSSC in digested sludge = | [5 empty] | 5%
f. | Yield Coefficient, Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized
g. | Endogenous coefficient, b = | [5 empty] | 0.03 | d-1
9 | Sludge dewatering
Assumptions,
a. | Sludge cake = | [5 empty] | 22% | solids
b. | Specific gravity of sludge = | [5 empty] | 1.123
c. | Solids capture = | [5 empty] | 90%
d. | Centrate BODC = | [5 empty] | 2000 | mg/L
10 | Other Important Values
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| TSSC of Supernatant = | [5 empty] | 0.5%
| Density of Water = | [5 empty] | 1000 | kg/m3
SOLUTION
1 | Convert the given constitient quantities to daily mass values
a. | BODM in influent :
| BODM = | [5 empty] | 9720 | kg/d | {(m3/d* g/m3) /(g/kg)}
| BODM of return flow = | [5 empty] | 908.3061 | kg/d
| BODM total = | [5 empty] | 10628.3061 | kg/d
b | TSSM in influent
| TSSM = | [5 empty] | 12960 | kg/d | {(m3/d* g/m3) /(g/kg)}
| TSSM of return flow = | [5 empty] | 1998.6967 | kg/d
| TSSM of combined flow = | [5 empty] | 14958.6967 | kg/d
c. | TSSM removed in grit = | [5 empty] | 648 | kg/d
| TSSC of Grit = | [5 empty] | 26500 | g/m3
| Flow rate = | [5 empty] | 24.4528 | m3/d
| BODC of Grit | [5 empty] | 767.652 | g/m3
| BODM of grit = | [5 empty] | 18.7713 | kg/d
d. | TSSM after grit removal ( influent to primary settling tank)
| TSSM = | [5 empty] | 14310.6967 | kg/d | {(m3/d* g/m3) /(g/kg)}
2 | Estimate the concentration of soluble BODC in the effluent using the following relationship :
| Eflluent BODC = Influent solube BODC escaping treatment (S) + BODC of effluent TSS | [10 empty] | Equation (8-26), Pg-726
a. | Determining BODC of effluent TSS
| Biodegradability portion of TSS (VSS/TSS)= | [5 empty] | 65%
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| Ratio of BODC by Ultimate BODC (BOD/UBOD)= | [5 empty] | 0.68
| BODC of Effluent TSSC = | [5 empty] | 18.8292 | g/m3 | {(g/g)/( g/g) *(g/g)/( g/g) *(g/g)/( g/g) }*g/m3
Eflluent BODC = Influent solube BODC escaping treatment + BODC of effluent TSS
20=S+13.8
| S= | [5 empty] | 1.1708 | g/m3
a. | Primary Sedimentation
i. | Operating Parameters
| BOD removal= | [5 empty] | 33%
| TSS removal = | [5 empty] | 50%
ii. | BODM removed = | [5 empty] | 3501.1465 | kg/d
iii. | BODM to secondary = | [5 empty] | 7108.3883 | kg/d
iv. | TSSM removed = | [5 empty] | 7155.3484 | kg/d
v. | TSSM to secondary = | [5 empty] | 7155.3484 | kg/d
b. | Determine volatile fraction of primary sludge
i. | Operating Parameters
| Concentration of primary sludge = | [5 empty] | 4%
| Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67%
| Assume Volatile fraction of grit = | [5 empty] | 3%
| VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
| VSSM in influent prior to grit removal = | [5 empty] | 10022.3268 | kg/d
| VSSM removed in grit chamber = | [5 empty] | 19.44 | kg/d
| VSSM in secondary influent = | [5 empty] | 6082.0461 | kg/d
| VSSM in primary sludge = | [5 empty] | 3920.8407 | kg/d
| Flow Rate of Primary Sludge = | [5 empty] | 178.8837 | m3/d
| Volatile Fraction in Primary Sludge = | [5 empty] | 54.8%
c. | Gravity Thickening of Primary Sludge
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
| Specific Gravity of Solids = | [5 empty] | 1
i. | Determine Flowrate of the Thickened Sludge = | [5 empty] | 101.3674 | m3/d
ii. | Determine flowrate recycled to the plant influent = | [5 empty] | 77.5163 | m3/d
iii. | Determine TSSM to the digestor = | [5 empty] | 6082.0461 | kg/d
iv. | Determine TSSM recycled to the plant influent = | [5 empty] | 1073.3023 | kg/d
v. | TSSC of the recycled flow = | [5 empty] | 13846.1538 | g/m3
vi. | BODC of the TSSC of recycled flow= | [5 empty] | 7326.1334 | g/m3
vii. | BODM of the recyled flow = | [5 empty] | 567.8946 | kg/d
viii. | BODC of the TSSC of flow going to digestor= | [5 empty] | 31746.5782 | g/m3
ix. | BODM of the digestor flow = | [5 empty] | 3218.0692 | kg/d
c. | Secondary Process
i. | Determining the secondary process operating parameters
| Flowrate = | [5 empty] | 32818.946 | m3/d
| The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
| Aeration tank volume, Vr = | [5 empty] | 7900 | m3
| Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
| Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
| Solids Retention Time, SRT = | [5 empty] | 10 | d
| BODM to secondary = | [5 empty] | 7108.3883 | kg/d
| BODC to secondary (S0) = | [5 empty] | 216.594 | g/m3 | {((kg/d)/(m3/d))/(kg/g)}
| Influent solube BODC escaping treatment (S) = | [5 empty] | 1.1708 | g/m3
| MLSS in Return Activated Sludge= | [5 empty] | 7000
| Mixed Liquor VSSC = | [5 empty] | 2796.6629 | g/m3 | Pg-600, Eq 7-42
| Mixed Liquor TSSC = | [5 empty] | 3495.8287 | g/m3
| Yobs = | [5 empty] | 0.3125 |  | Pg-603, Eq 7-59
ii. | Determine Effluent Mass Quantities
| BODM = | [5 empty] | 656.3789 | kg/d
| TSSM = | [5 empty] | 984.5684 | kg/d
iii. | Estimate Mass of Volatile solids produced in the activated sludge process that must be waste.
| PX,VSS = | [5 empty] | 2209.3637 | kg/d | Pg-720 Eq 8-19
iv. | Estimate the TSSM that must be wasted
| TSSM = | [5 empty] | 2761.7046 | kg/d
v. | Estimate the waste quantities discharged to the thicker. It is assumed that the wasting is from the secondary clarifier
| TSSM = | [5 empty] | 1777.1363 | kg/d
| Flowrate = | [5 empty] | 253.8766 | m3/d
d. | Flotation Thickeners
i. | Operating Parameters
| Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
| ( specific gravity of the solids ) = | [5 empty] | 1
ii. | Determine flowrate of the thickened sludge
| Solid captured by thickener = | [5 empty] | 1599.4226 | kg/d
| Flowrate = | [5 empty] | 31.9885 | m3/d
iii. | Determine Flowrate recyled to the plant influent
| Recycled Flowrate = | [5 empty] | 221.8882 | m3/d
iv. | Determine the TSSM to the digester
| TSSM = | [5 empty] | 1599.4226 | kg/d
v | Determine the BODC of the TSSC going to digester
| TSSC = | [5 empty] | 50000 | g/m3
| BODC of the TSSC = | [5 empty] | 38624 | g/m3
| BODM = | [5 empty] | 1235.522 | kg/d
vi | Determine the TSSM recyled to the plant influent
| TSSM = | [5 empty] | 177.7136 | kg/d
vii | Determine the BODC of the TSSC in the recyled flow
| TSSC in the recyled flow = | [5 empty] | 800.9153 | g/m3
| BODC of the TSSC = | [5 empty] | 502.6865 | g/m3 |  |  | Equation (8-26), Pg-726
| BODM = | [5 empty] | 111.5402 | kg/d
e. | Sludge Digestion
i. | Operating Parameters
| SRT = | [5 empty] | 20 | d
| Volatile Solids Reduction, VSR = | [5 empty] | 60%
| BODC in digester supernatant = | [5 empty] | 1000 | g/m3
| TSSC in digested sludge = | [5 empty] | 5%
ii. | Determine the solids fed to the digester and the corresponding flowrate.
TSSM = Solids fed from gravity thickener and solids fed from thickener
| TSSM = | [5 empty] | 7681.4687 | kg/d
| Total Flowrate = | [5 empty] | 133.3559 | m3/d
iii. | Determine the VSSM fed to the digester
| VSSM = | [5 empty] | 4612.2527 | kg/d
| Percentage VSSM in mixture fed to digester = | [5 empty] | 60.04%
iv. | Determine the VSS destroyed
| VSSM = | [5 empty] | 2767.3516 | kg/d
v. | Determine the mass flowrate to the digester
| Mass Flow from Primary Sludge = | [5 empty] | 101367.4351 | kg/d |  | (Unitary method, if 6% has a mass of 5443.2 kg, how much does 100% have)
| Mass Flow from Thickened Activated Sludge = | [5 empty] | 31988.4528 | kg/d |  | (Unitary method, if 4% has a mass of 1433 kg, how much does 100% have)
Parameters for Digester
| Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized | [5 empty] | Pg,1506,1507, Eq 13-12, 13-13
| b = | [5 empty] | 0.03 | d-1
| S0= | [5 empty] | 4453.5912 | kg/d | (Combined BODC from Primary and Secondary Sludge)
| S= | [5 empty] | 1781.4365 | kg/d | BODC after digestion based on percentage reduction of VSS
| Q= | [5 empty] | 133.3559 | m3/d | Combined Flow rate
| SRT = | [5 empty] | 20 | d
| PX = | [5 empty] | 133.6077 | kg/d | Net Mass of Cell tissue produced per day
| VCH4 = | [5 empty] | 868.8511 | m3/d
| VGAS = | [5 empty] | 1336.694 | m3/d | (Assuming 65% of biogas as methane)
| Biogas Mass = | [5 empty] | 1497.0973 | kg/d | (Assuming density of biogas as 1.12 kg/m3)
vi. | Determine the mass quantities of gas and sludge after digestion.
Fixed Solids = TSSM - VSSM
| Fixed Solids = | [5 empty] | 3069.216 | kg/d
| TSSM in digested sludge= | [5 empty] | 4914.1171 | kg/d
Mass Balance of Digested Output
| Mass IN = | [5 empty] | 133355.8879 | kg/d
| Gas Produced = | [5 empty] | 1497.0973 | kg/d
| Mass Out = | [5 empty] | 131858.7906 | kg/d | (Solids and Liquid)
vii. | Determine the flowrate distribution between the supernatant at 0.5% solids and digested Sludge at 5% solids. Let X = TSS of Supernatant
| TSSC of Supernatant = | [5 empty] | 0.5%
| TSSC of Digested Sludge = | [5 empty] | 5%
Mass Flow of Supernatant + Mass Flow of Digested Solids = Mass Out
Let X be TSSM of Supernatant
{(X/0.005)+((4443-X)/0.05)}=123729
Solve for X
| X = | [5 empty] | 186.5358 | kg/d
| TSSM of Supernatant = | [5 empty] | 186.5358 | kg/d
| TSSM of Digested Sludge = | [5 empty] | 4727.5813 | kg/d
| Supernatant Flowrate = | [5 empty] | 37.3072 | m3/d
| Digested Sludge Flowrate = | [5 empty] | 94.5516 | m3/d
viii. | Establish the characteristics of the recycled flow
| Flowrate = | [5 empty] | 37.3072 | m3/d
| BODM of Supernatant = | [5 empty] | 37.3072 | kg/d
| TSSM of Supernatant = | [5 empty] | 186.5358 | kg/d
f. | Sludge Dewatering
i. | Operating Parameters for centrifuge :
| Sludge cake = | [5 empty] | 22% | solids
| Specific gravity of sludge = | [5 empty] | 1.123
| Solids capture = | [5 empty] | 90%
| Centrate BODC = | [5 empty] | 2000 | mg/L
| Density of Water = | [5 empty] | 1000 | kg/m3
ii. | Determine the Sludge-cake characteristics.
| Solids = | [5 empty] | 4254.8232 | kg/d
| Flow rate = | [5 empty] | 17.2218 | m3/d
iii. | Determine the Centrate Characteristics
| Flowrate = | [5 empty] | 77.3298 | m3/d
| BODM = | [5 empty] | 154.6596 | kg/d
| TSSM = | [5 empty] | 472.7581 | kg/d
g. | Prepare a summary table of the recycle flows and waste characteristics for the first iteration
Incremental change from previous iteration
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Gravity Thickener | 77.5163 | 567.8946 | 1073.3023 | -4.6715 | -30.604 | -64.6822
| Flotation Thickener | 221.8882 | 111.5402 | 177.7136 | 4.3297 | 2.1765 | 3.4677
| Digester Supernatant | 37.3072 | 37.3072 | 186.5358 | -0.64848 | -0.64848 | -3.2424
| Centrate | 77.3298 | 154.6596 | 472.7581 | -3.9143 | -7.8286 | -23.93
| Totals | 414.0414 | 871.4015 | 1910.3098 | -4.9046 | -36.9045 | -88.3869
[5 empty] | -1.185% | -4.235% | -4.627%

## 2nd Iteration
Preparation of a Solids Mass Balance for 32.4 MLD GWWTP in Kathmandu
1 | Definition of terms
BODC = biochemical oxygen demand expressed as a concentration, g/m3
BODM = biochemical oxygen demand expressed as a mass, kg/d
TSSC = total suspended solids expressed as a concentration, g/m3
TSSM = total suspended solids expressed as a mass, kg/d
2 | Wastewater flowrates
a. | Annual average flowrate | [5 empty] | 32400 | m3/d
b. | Return Flowrate | [5 empty] | 364.508 | m3/d
c. | Annual average Flowrate | [5 empty] | 32764.508 | m3/d
3 | Influent characteristics | [10 empty] | Legend
a. | BODC = | [5 empty] | 300 | g/m3 |  |  |  |  | Real Values Taken From WWTP
b. | TSSC = | [5 empty] | 400 | g/m3 |  |  |  |  | Values taken from Metcalf & Eddy
c. | Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67% | [5 empty] | Computed Values
| TSS removed in grit = | [5 empty] | 5% | [5 empty] | Referenced Values
d. | TSSC after grit removal = | [5 empty] | 380 | g/m3
e. | Assume Volatile fraction of grit = | [5 empty] | 3%
| Specific Gravity of Grit = | [5 empty] | 2.65 | kg/m3
| Solids Concentration in Grit = | [5 empty] | 1%
4 | Sludge and biosolids characteristics
a. | Concentration of primary sludge = | [5 empty] | 4%
b. | Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
c. | (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
d. | Total suspended solids in digested sludge = | [5 empty] | 5%
e. | Special Gravity of Solids = | [5 empty] | 1
f. | Fraction of the biological solids that are biodegradable = | [5 empty] | 65%
g. | The value of BODC can be obtained by multiplying the value of UBOD by a factor of | [5 empty] | 0.68
5 | Effluent characteristics
a. | BODC = | [5 empty] | 10 | g/m3
b. | TSSC = | [5 empty] | 10 | g/m3
Secondary Clarifier Outlet characteristics
a. | BODC = | [5 empty] | 20 | g/m3
b. | TSSC = | [5 empty] | 30 | g/m3
6 | Primary clarifier
Assumtions,
a. | BOD removal= | [5 empty] | 33%
b. | TSS removal = | [5 empty] | 50%
c. | VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
7 | Secondary treatment
Assumption,
a. | The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
b. | Aeration tank volume, Vr = | [5 empty] | 7900 | m3
c. | Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
d. | Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
e. | Solids Retention Time, SRT = | [5 empty] | 10 | d
f. | MLSS in Return Activated Sludge= | [5 empty] | 7000 | g/m3
8 | Sludge digestion
Assumption,
a. | SRT = | [5 empty] | 20 | d
b. | Volatile Solids Reduction, VSR = | [5 empty] | 60%
d. | BODC in digester supernatant = | [5 empty] | 1000 | g/m3
e. | TSSC in digested sludge = | [5 empty] | 5%
f. | Yield Coefficient, Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized
g. | Endogenous coefficient, b = | [5 empty] | 0.03 | d-1
9 | Sludge dewatering
Assumptions,
a. | Sludge cake = | [5 empty] | 22% | solids
b. | Specific gravity of sludge = | [5 empty] | 1.123
c. | Solids capture = | [5 empty] | 90%
d. | Centrate BODC = | [5 empty] | 2000 | mg/L
10 | Other Important Values
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| TSSC of Supernatant = | [5 empty] | 0.5%
| Density of Water = | [5 empty] | 1000 | kg/m3
SOLUTION
1 | Convert the given constitient quantities to daily mass values
a. | BODM in influent :
| BODM = | [5 empty] | 9720 | kg/d | {(m3/d* g/m3) /(g/kg)}
| BODM of return flow = | [5 empty] | 769.473 | kg/d
| BODM total = | [5 empty] | 10489.473 | kg/d
b | TSSM in influent
| TSSM = | [5 empty] | 12960 | kg/d | {(m3/d* g/m3) /(g/kg)}
| TSSM of return flow = | [5 empty] | 2861.1255 | kg/d
| TSSM of combined flow = | [5 empty] | 15821.1255 | kg/d
c. | TSSM removed in grit = | [5 empty] | 648 | kg/d
| TSSC of Grit = | [5 empty] | 26500 | g/m3
| Flow rate = | [5 empty] | 24.4528 | m3/d
| BODC of Grit | [5 empty] | 767.652 | g/m3
| BODM of grit = | [5 empty] | 18.7713 | kg/d
d. | TSSM after grit removal ( influent to primary settling tank)
| TSSM = | [5 empty] | 15173.1255 | kg/d | {(m3/d* g/m3) /(g/kg)}
2 | Estimate the concentration of soluble BODC in the effluent using the following relationship :
| Eflluent BODC = Influent solube BODC escaping treatment (S) + BODC of effluent TSS | [10 empty] | Equation (8-26), Pg-726
a. | Determining BODC of effluent TSS
| Biodegradability portion of TSS (VSS/TSS)= | [5 empty] | 65%
| UBOD used per gram VSS Consumed (UBOD/VSS) = | [5 empty] | 1.42
| Ratio of BODC by Ultimate BODC (BOD/UBOD)= | [5 empty] | 0.68
| BODC of Effluent TSSC = | [5 empty] | 18.8292 | g/m3 | {(g/g)/( g/g) *(g/g)/( g/g) *(g/g)/( g/g) }*g/m3
Eflluent BODC = Influent solube BODC escaping treatment + BODC of effluent TSS
20=S+13.8
| S= | [5 empty] | 1.1708 | g/m3
a. | Primary Sedimentation
i. | Operating Parameters
| BOD removal= | [5 empty] | 33%
| TSS removal = | [5 empty] | 50%
ii. | BODM removed = | [5 empty] | 3455.3316 | kg/d
iii. | BODM to secondary = | [5 empty] | 7015.3702 | kg/d
iv. | TSSM removed = | [5 empty] | 7586.5628 | kg/d
v. | TSSM to secondary = | [5 empty] | 7586.5628 | kg/d
b. | Determine volatile fraction of primary sludge
i. | Operating Parameters
| Concentration of primary sludge = | [5 empty] | 4%
| Assume ( VSSC/TSSC) ratio in influent = | [5 empty] | 67%
| Assume Volatile fraction of grit = | [5 empty] | 3%
| VSSC/ TSSC ratio in primary effluent going to the secondary treatment = | [5 empty] | 85%
| VSSM in influent prior to grit removal = | [5 empty] | 10600.1541 | kg/d
| VSSM removed in grit chamber = | [5 empty] | 19.44 | kg/d
| VSSM in secondary influent = | [5 empty] | 6448.5784 | kg/d
| VSSM in primary sludge = | [5 empty] | 4132.1358 | kg/d
| Flow Rate of Primary Sludge = | [5 empty] | 189.6641 | m3/d
| Volatile Fraction in Primary Sludge = | [5 empty] | 54.47%
c. | Gravity Thickening of Primary Sludge
| (Solids Capture in Gravity Thickener) = | [5 empty] | 85%
| Concentration of Thickened sludge = | [5 empty] | 6%
| Specific Gravity of Solids = | [5 empty] | 1
i. | Determine Flowrate of the Thickened Sludge = | [5 empty] | 107.4763 | m3/d
ii. | Determine flowrate recycled to the plant influent = | [5 empty] | 82.1878 | m3/d
iii. | Determine TSSM to the digestor = | [5 empty] | 6448.5784 | kg/d
iv. | Determine TSSM recycled to the plant influent = | [5 empty] | 1137.9844 | kg/d
v. | TSSC of the recycled flow = | [5 empty] | 13846.1538 | g/m3
vi. | BODC of the TSSC of recycled flow= | [5 empty] | 7282.0882 | g/m3
vii. | BODM of the recyled flow = | [5 empty] | 598.4985 | kg/d
viii. | BODC of the TSSC of flow going to digestor= | [5 empty] | 31555.7156 | g/m3
ix. | BODM of the digestor flow = | [5 empty] | 3391.4917 | kg/d
c. | Secondary Process
i. | Determining the secondary process operating parameters
| Flowrate = | [5 empty] | 32764.508 | m3/d
| The mixed-liquor VSSC/ TSSC ratio = | [5 empty] | 0.8
| Aeration tank volume, Vr = | [5 empty] | 7900 | m3
| Yeld Cofficient, Y = | [5 empty] | 0.5 | kg/kg
| Decay Co-efficient, b = | [5 empty] | 0.06 | d-1
| Solids Retention Time, SRT = | [5 empty] | 10 | d
| BODM to secondary = | [5 empty] | 7015.3702 | kg/d
| BODC to secondary (S0) = | [5 empty] | 214.1149 | g/m3 | {((kg/d)/(m3/d))/(kg/g)}
| Influent solube BODC escaping treatment (S) = | [5 empty] | 1.1708 | g/m3
| MLSS in Return Activated Sludge= | [5 empty] | 7000
| Mixed Liquor VSSC = | [5 empty] | 2759.893 | g/m3 | Pg-600, Eq 7-42
| Mixed Liquor TSSC = | [5 empty] | 3449.8662 | g/m3
| Yobs = | [5 empty] | 0.3125 |  | Pg-603, Eq 7-59
ii. | Determine Effluent Mass Quantities
| BODM = | [5 empty] | 655.2902 | kg/d
| TSSM = | [5 empty] | 982.9352 | kg/d
iii. | Estimate Mass of Volatile solids produced in the activated sludge process that must be waste.
| PX,VSS = | [5 empty] | 2180.3155 | kg/d | Pg-720 Eq 8-19
iv. | Estimate the TSSM that must be wasted
| TSSM = | [5 empty] | 2725.3943 | kg/d
v. | Estimate the waste quantities discharged to the thicker. It is assumed that the wasting is from the secondary clarifier
| TSSM = | [5 empty] | 1742.4591 | kg/d
| Flowrate = | [5 empty] | 248.9227 | m3/d
d. | Flotation Thickeners
i. | Operating Parameters
| Concentration of thickened waste-activated sludge = | [5 empty] | 5%
| (Assume solids capture in the flotation thickeners )= | [5 empty] | 90%
| ( specific gravity of the solids ) = | [5 empty] | 1
ii. | Determine flowrate of the thickened sludge
| Solid captured by thickener = | [5 empty] | 1568.2132 | kg/d
| Flowrate = | [5 empty] | 31.3643 | m3/d
iii. | Determine Flowrate recyled to the plant influent
| Recycled Flowrate = | [5 empty] | 217.5585 | m3/d
iv. | Determine the TSSM to the digester
| TSSM = | [5 empty] | 1568.2132 | kg/d
v | Determine the BODC of the TSSC going to digester
| TSSC = | [5 empty] | 50000 | g/m3
| BODC of the TSSC = | [5 empty] | 38624 | g/m3
| BODM = | [5 empty] | 1211.4133 | kg/d
vi | Determine the TSSM recyled to the plant influent
| TSSM = | [5 empty] | 174.2459 | kg/d
vii | Determine the BODC of the TSSC in the recyled flow
| TSSC in the recyled flow = | [5 empty] | 800.9153 | g/m3
| BODC of the TSSC = | [5 empty] | 502.6865 | g/m3 |  |  | Equation (8-26), Pg-726
| BODM = | [5 empty] | 109.3637 | kg/d
e. | Sludge Digestion
i. | Operating Parameters
| SRT = | [5 empty] | 20 | d
| Volatile Solids Reduction, VSR = | [5 empty] | 60%
| BODC in digester supernatant = | [5 empty] | 1000 | g/m3
| TSSC in digested sludge = | [5 empty] | 5%
ii. | Determine the solids fed to the digester and the corresponding flowrate.
TSSM = Solids fed from gravity thickener and solids fed from thickener
| TSSM = | [5 empty] | 8016.7915 | kg/d
| Total Flowrate = | [5 empty] | 138.8406 | m3/d
iii. | Determine the VSSM fed to the digester
| VSSM = | [5 empty] | 4766.8859 | kg/d
| Percentage VSSM in mixture fed to digester = | [5 empty] | 59.46%
iv. | Determine the VSS destroyed
| VSSM = | [5 empty] | 2860.1316 | kg/d
v. | Determine the mass flowrate to the digester
| Mass Flow from Primary Sludge = | [5 empty] | 107476.3059 | kg/d |  | (Unitary method, if 6% has a mass of 5443.2 kg, how much does 100% have)
| Mass Flow from Thickened Activated Sludge = | [5 empty] | 31364.2637 | kg/d |  | (Unitary method, if 4% has a mass of 1433 kg, how much does 100% have)
Parameters for Digester
| Y= | [5 empty] | 0.08 | kg VSS/kg bCOD utilized | [5 empty] | Pg,1506,1507, Eq 13-12, 13-13
| b = | [5 empty] | 0.03 | d-1
| S0= | [5 empty] | 4602.9051 | kg/d | (Combined BODC from Primary and Secondary Sludge)
| S= | [5 empty] | 1841.162 | kg/d | BODC after digestion based on percentage reduction of VSS
| Q= | [5 empty] | 138.8406 | m3/d | Combined Flow rate
| SRT = | [5 empty] | 20 | d
| PX = | [5 empty] | 138.0872 | kg/d | Net Mass of Cell tissue produced per day
| VCH4 = | [5 empty] | 897.9807 | m3/d
| VGAS = | [5 empty] | 1381.5088 | m3/d | (Assuming 65% of biogas as methane)
| Biogas Mass = | [5 empty] | 1547.2899 | kg/d | (Assuming density of biogas as 1.12 kg/m3)
vi. | Determine the mass quantities of gas and sludge after digestion.
Fixed Solids = TSSM - VSSM
| Fixed Solids = | [5 empty] | 3249.9056 | kg/d
| TSSM in digested sludge= | [5 empty] | 5156.66 | kg/d
Mass Balance of Digested Output
| Mass IN = | [5 empty] | 138840.5696 | kg/d
| Gas Produced = | [5 empty] | 1547.2899 | kg/d
| Mass Out = | [5 empty] | 137293.2797 | kg/d | (Solids and Liquid)
vii. | Determine the flowrate distribution between the supernatant at 0.5% solids and digested Sludge at 5% solids. Let X = TSS of Supernatant
| TSSC of Supernatant = | [5 empty] | 0.5%
| TSSC of Digested Sludge = | [5 empty] | 5%
Mass Flow of Supernatant + Mass Flow of Digested Solids = Mass Out
Let X be TSSM of Supernatant
{(X/0.005)+((4443-X)/0.05)}=123729
Solve for X
| X = | [5 empty] | 189.7782 | kg/d
| TSSM of Supernatant = | [5 empty] | 189.7782 | kg/d
| TSSM of Digested Sludge = | [5 empty] | 4966.8817 | kg/d
| Supernatant Flowrate = | [5 empty] | 37.9556 | m3/d
| Digested Sludge Flowrate = | [5 empty] | 99.3376 | m3/d
viii. | Establish the characteristics of the recycled flow
| Flowrate = | [5 empty] | 37.9556 | m3/d
| BODM of Supernatant = | [5 empty] | 37.9556 | kg/d
| TSSM of Supernatant = | [5 empty] | 189.7782 | kg/d
f. | Sludge Dewatering
i. | Operating Parameters for centrifuge :
| Sludge cake = | [5 empty] | 22% | solids
| Specific gravity of sludge = | [5 empty] | 1.123
| Solids capture = | [5 empty] | 90%
| Centrate BODC = | [5 empty] | 2000 | mg/L
| Density of Water = | [5 empty] | 1000 | kg/m3
ii. | Determine the Sludge-cake characteristics.
| Solids = | [5 empty] | 4470.1936 | kg/d
| Flow rate = | [5 empty] | 18.0936 | m3/d
iii. | Determine the Centrate Characteristics
| Flowrate = | [5 empty] | 81.2441 | m3/d
| BODM = | [5 empty] | 162.4882 | kg/d
| TSSM = | [5 empty] | 496.6882 | kg/d
g. | Prepare a summary table of the recycle flows and waste characteristics for the first iteration
Incremental change from previous iteration
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Gravity Thickener | 82.1878 | 598.4985 | 1137.9844 | 15.4978 | 101.5293 | 214.5844
| Flotation Thickener | 217.5585 | 109.3637 | 174.2459 | 23.7583 | 11.943 | 19.0284
| Digester Supernatant | 37.9556 | 37.9556 | 189.7782 | 5.0032 | 5.0032 | 25.0159
| Centrate | 81.2441 | 162.4882 | 496.6882 | 10.1788 | 20.3576 | -1121.0575
| Totals | 418.946 | 908.3061 | 1998.6967 | 54.438 | 138.833 | -862.4288
[5 empty] | 12.99% | 15.28% | -43.15%

## 1st Iteration
Preparation of a Solids Mass Balance for 32.4 MLD GWWTP in Kathmandu
1 | Definition of terms
BODC = biochemical oxygen demand expressed as a concentration, g/m3
BODM = biochemical oxygen demand expressed as a mass, kg/d
TSSC = total suspended solids expressed as a concentration, g/m3
TSSM = total suspended solids expressed as a mass, kg/d
2 | Wastewater flowrates
a. | Annual average flowrate |  |  |  | 32400 | m3/d
b. | Return Flowrate |  |  |  | 0 | m3/d
c. | Total average flowrate = |  |  |  | 32400 | m3/d
3 | Influent characteristics | [8 empty] | Legend |  |  | Parameters taken as Reference
a. | BODC = |  |  |  | 300 | g/m3 |  |  |  |  | Real Values Taken From WWTP |  | Parameters taken from GWWTP | Parameters taken From Metcalf & Eddy
b. | TSSC = |  |  |  | 400 | g/m3 |  |  |  |  | Values taken from Metcalf & Eddy |  | Annual average flowrate | ( VSSC/TSSC) ratio in influent
c. | Assume ( VSSC/TSSC) ratio in influent = |  |  |  | 67% | [5 empty] | Computed Values |  | Influent characteristics | The mixed-liquor VSSC/ TSSC ratio
| TSS removed in grit = |  |  |  | 5% | [5 empty] | Referenced Values |  | TSS removed in grit | (VSSC/ TSSC) ratio going to secondary treatment
d. | TSSC after grit removal = |  |  |  | 380 | g/m3 | [6 empty] | Volatile fraction of grit | Yeld Cofficient for Aeration Tank
e. | Assume Volatile fraction of grit = |  |  |  | 3% | [7 empty] | Specific Gravity of Grit | Decay Co-efficient for Aeration Tank
| Specific Gravity of Grit = |  |  |  | 2.65 | kg/m3 | [6 empty] | Solids Concentration in Grit | Solids Retention Time for Aeration Tank
| Solids Concentration in Grit = |  |  |  | 1% | [7 empty] | BOD removal in Primary Sedimentation | Special Gravity of Solids
4 | Sludge and biosolids characteristics | [11 empty] | TSS removal in Primary Sedimentation | Biodegradability of biological solids
a. | Concentration of primary sludge = |  |  |  | 4% | [7 empty] | Concentration of primary sludge | Ratio of ( BODC/UBOD)
b. | Concentration of thickened waste-activated sludge = |  |  |  | 5% | [7 empty] | (Solids Capture in Gravity Thickener) | Ratio of (UBOD/VSS)
| (Solids Capture in Gravity Thickener) = |  |  |  | 85% | [7 empty] | Concentration of Thickened sludge | Yield Coefficient for Digestor
| Concentration of Thickened sludge = |  |  |  | 6% | [7 empty] | MLSS in Return Activated Sludge | Endogenous coefficient for Digestor
c. | (Assume solids capture in the flotation thickeners )= |  |  |  | 90% | [7 empty] | Solids capture in the flotation thickeners | BODC in digester supernatant
d. | Total suspended solids in digested sludge = |  |  |  | 5% | [7 empty] | Concentration of thickened WAS | TSSC of Supernatant
e. | Special Gravity of Solids = |  |  |  | 1 | [7 empty] | Secondary Clarifier Outlet characteristics | Centrate BODC
f. | Fraction of the biological solids that are biodegradable = |  |  |  | 65% | [7 empty] | Effluent characteristics | Density of Water
g. | The value of BODC can be obtained by multiplying the value of UBOD by a factor of |  |  |  | 0.68 | [7 empty] | Solids Rentention Rate in Digestor
5 | Effluent characteristics | [11 empty] | Volatile Solids Reduction
a. | BODC = |  |  |  | 10 | g/m3 | [6 empty] | Total suspended solids in digested sludge
b. | TSSC = |  |  |  | 10 | g/m3 | [6 empty] | BODC in digester supernatant
| Secondary Clarifier Outlet characteristics | [11 empty] | TSSC in digested sludge
c. | BODC = |  |  |  | 20 | g/m3 | [6 empty] | Sludge cake
d. | TSSC = |  |  |  | 30 | g/m3 | [6 empty] | Specific gravity of sludge
6 | Primary clarifier | [11 empty] | Solids capture in centrifuge
Assumtions,
a. | BOD removal= |  |  |  | 33%
b. | TSS removal = |  |  |  | 50%
c. | VSSC/ TSSC ratio in primary effluent going to the secondary treatment = |  |  |  | 85%
7 | Secondary treatment
Assumption,
a. | The mixed-liquor VSSC/ TSSC ratio = |  |  |  | 0.8
b. | Aeration tank volume, Vr = |  |  |  | 7900 | m3
c. | Yeld Cofficient, Y = |  |  |  | 0.5 | kg/kg
d. | Decay Co-efficient, b = |  |  |  | 0.06 | d-1
e. | Solids Retention Time, SRT = |  |  |  | 10 | d
f. | MLSS in Return Activated Sludge= |  |  |  | 7000 | g/m3
8 | Sludge digestion
Assumption,
a. | SRT = |  |  |  | 20 | d
b. | Volatile Solids Reduction, VSR = |  |  |  | 60%
d. | BODC in digester supernatant = |  |  |  | 1000 | g/m3
e. | TSSC in digested sludge = |  |  |  | 5%
f. | Yield Coefficient, Y= |  |  |  | 0.08 | kg VSS/kg bCOD utilized
g. | Endogenous coefficient, b = |  |  |  | 0.03 | d-1
9 | Sludge dewatering
Assumptions,
a. | Sludge cake = |  |  |  | 22% | solids
b. | Specific gravity of sludge = |  |  |  | 1.123
c. | Solids capture = |  |  |  | 60%
d. | Centrate BODC = |  |  |  | 2000 | mg/L
10 | Other Important Values
| UBOD used per gram VSS Consumed (UBOD/VSS) = |  |  |  | 1.42
| TSSC of Supernatant = |  |  |  | 0.5%
| Density of Water = |  |  |  | 1000 | kg/m3
SOLUTION
1 | Convert the given constitient quantities to daily mass values
a. | BODM in influent :
| BODM = |  |  |  | 9720 | kg/d | {(m3/d* g/m3) /(g/kg)}
| BODM of return flow = |  |  |  |  | kg/d
| BODM total = |  |  |  | 9720
b | TSSM in influent
| TSSM = |  |  |  | 12960 | kg/d | {(m3/d* g/m3) /(g/kg)}
| TSSM of return flow = |  |  |  | 0 | kg/d
| TSSM of combined flow = |  |  |  | 12960 | kg/d
c. | TSSM removed in grit = |  |  |  | 648 | kg/d
| TSSC of Grit = |  |  |  | 26500 | g/m3
| Flow rate = |  |  |  | 24.4528 | m3/d
| BODC of Grit |  |  |  | 767.652 | g/m3
| BODM of grit = |  |  |  | 18.7713 | kg/d
d. | TSSM after grit removal ( influent to primary settling tank)
| TSSM = |  |  |  | 12312 | kg/d | {(m3/d* g/m3) /(g/kg)}
2 | Estimate the concentration of soluble BODC in the effluent using the following relationship :
| Eflluent BODC = Influent solube BODC escaping treatment (S) + BODC of effluent TSS | [8 empty] | Equation (8-26), Pg-726
a. | Determining BODC of effluent TSS
| Biodegradability portion of TSS (VSS/TSS)= |  |  |  | 65%
| UBOD used per gram VSS Consumed (UBOD/VSS) = |  |  |  | 1.42
| Ratio of BODC by Ultimate BODC (BOD/UBOD)= |  |  |  | 0.68
| BODC of Effluent TSSC = |  |  |  | 18.8292 | g/m3 | {(g/g)/( g/g) *(g/g)/( g/g) *(g/g)/( g/g) }*g/m3
Eflluent BODC = Influent solube BODC escaping treatment + BODC of effluent TSS
20=S+13.8
| S= |  |  |  | 1.1708 | g/m3
a. | Primary Sedimentation
i. | Operating Parameters
| BOD removal= |  |  |  | 33%
| TSS removal = |  |  |  | 50%
ii. | BODM removed = |  |  |  | 3201.4055 | kg/d
iii. | BODM to secondary = |  |  |  | 6499.8233 | kg/d
iv. | TSSM removed = |  |  |  | 6156 | kg/d
v. | TSSM to secondary = |  |  |  | 6156 | kg/d
b. | Determine volatile fraction of primary sludge
i. | Operating Parameters
| Concentration of primary sludge = |  |  |  | 4%
| Assume ( VSSC/TSSC) ratio in influent = |  |  |  | 67%
| Assume Volatile fraction of grit = |  |  |  | 3%
| VSSC/ TSSC ratio in primary effluent going to the secondary treatment = |  |  |  | 85%
| VSSM in influent prior to grit removal = |  |  |  | 8683.2 | kg/d
| VSSM removed in grit chamber = |  |  |  | 19.44 | kg/d
| VSSM in secondary influent = |  |  |  | 5232.6 | kg/d
| VSSM in primary sludge = |  |  |  | 3431.16 | kg/d
| Flow Rate of Primary Sludge = |  |  |  | 153.9 | m3/d
| Volatile Fraction in Primary Sludge = |  |  |  | 55.74%
c. | Gravity Thickening of Primary Sludge
| (Solids Capture in Gravity Thickener) = |  |  |  | 85%
| Concentration of Thickened sludge = |  |  |  | 6%
| Specific Gravity of Solids = |  |  |  | 1
i. | Determine Flowrate of the Thickened Sludge = |  |  |  | 87.21 | m3/d
ii. | Determine flowrate recycled to the plant influent = |  |  |  | 66.69 | m3/d
iii. | Determine TSSM to the digestor = |  |  |  | 5232.6 | kg/d
iv. | Determine TSSM recycled to the plant influent = |  |  |  | 923.4 | kg/d
v. | TSSC of the recycled flow = |  |  |  | 13846.1538 | g/m3
vi. | BODC of the TSSC of recycled flow= |  |  |  | 7451.93 | g/m3
vii. | BODM of the recyled flow = |  |  |  | 496.9692 | kg/d
viii. | BODC of the TSSC of flow going to digestor= |  |  |  | 32291.6968 | g/m3
ix. | BODM of the digestor flow = |  |  |  | 2816.1589 | kg/d
c. | Secondary Process
i. | Determining the secondary process operating parameters
| Flowrate = |  |  |  | 32400 | m3/d
| The mixed-liquor VSSC/ TSSC ratio = |  |  |  | 0.8
| Aeration tank volume, Vr = |  |  |  | 7900 | m3
| Yeld Cofficient, Y = |  |  |  | 0.5 | kg/kg
| Decay Co-efficient, b = |  |  |  | 0.06 | d-1
| Solids Retention Time, SRT = |  |  |  | 10 | d
| BODM to secondary = |  |  |  | 6499.8233 | kg/d
| BODC to secondary (S0) = |  |  |  | 200.6118 | g/m3 | {((kg/d)/(m3/d))/(kg/g)}
| Influent solube BODC escaping treatment (S) = |  |  |  | 1.1708 | g/m3
| MLSS in Return Activated Sludge= |  |  |  | 7000
| Mixed Liquor VSSC = |  |  |  | 2556.1271 | g/m3 | Pg-600, Eq 7-42
| Mixed Liquor TSSC = |  |  |  | 3195.1589 | g/m3
| Yobs = |  |  |  | 0.3125 |  | Pg-603, Eq 7-59
ii. | Determine Effluent Mass Quantities
| BODM = |  |  |  | 648 | kg/d
| TSSM = |  |  |  | 972 | kg/d
iii. | Estimate Mass of Volatile solids produced in the activated sludge process that must be waste.
| PX,VSS = |  |  |  | 2019.3404 | kg/d | Pg-720 Eq 8-19
iv. | Estimate the TSSM that must be wasted
| TSSM = |  |  |  | 2524.1755 | kg/d
v. | Estimate the waste quantities discharged to the thicker. It is assumed that the wasting is from the secondary clarifier
| TSSM = |  |  |  | 1552.1755 | kg/d
| Flowrate = |  |  |  | 221.7394 | m3/d
d. | Flotation Thickeners
i. | Operating Parameters
| Concentration of thickened waste-activated sludge = |  |  |  | 5%
| (Assume solids capture in the flotation thickeners )= |  |  |  | 90%
| ( specific gravity of the solids ) = |  |  |  | 1
ii. | Determine flowrate of the thickened sludge
| Solid captured by thickener = |  |  |  | 1396.958 | kg/d
| Flowrate = |  |  |  | 27.9392 | m3/d
iii. | Determine Flowrate recyled to the plant influent
| Recycled Flowrate = |  |  |  | 193.8002 | m3/d
iv. | Determine the TSSM to the digester
| TSSM = |  |  |  | 1396.958 | kg/d
v | Determine the BODC of the TSSC going to digester
| TSSC = |  |  |  | 50000 | g/m3
| BODC of the TSSC = |  |  |  | 38624 | g/m3
| BODM = |  |  |  | 1079.1221 | kg/d
vi | Determine the TSSM recyled to the plant influent
| TSSM = |  |  |  | 155.2176 | kg/d
vii | Determine the BODC of the TSSC in the recyled flow
| TSSC in the recyled flow = |  |  |  | 800.9153 | g/m3
| BODC of the TSSC = |  |  |  | 502.6865 | g/m3 |  |  | Equation (8-26), Pg-726
| BODM = |  |  |  | 97.4207 | kg/d
e. | Sludge Digestion
i. | Operating Parameters
| SRT = |  |  |  | 20 | d
| Volatile Solids Reduction, VSR = |  |  |  | 60%
| BODC in digester supernatant = |  |  |  | 1000 | g/m3
| TSSC in digested sludge = |  |  |  | 5%
ii. | Determine the solids fed to the digester and the corresponding flowrate.
TSSM = Solids fed from gravity thickener and solids fed from thickener
| TSSM = |  |  |  | 6629.558 | kg/d
| Total Flowrate = |  |  |  | 115.1492 | m3/d
iii. | Determine the VSSM fed to the digester
| VSSM = |  |  |  | 4034.0524 | kg/d
| Percentage VSSM in mixture fed to digester = |  |  |  | 60.85%
iv. | Determine the VSS destroyed
| VSSM = |  |  |  | 2420.4314 | kg/d
v. | Determine the mass flowrate to the digester
| Mass Flow from Primary Sludge = |  |  |  | 87210 | kg/d |  | (Unitary method, if 6% has a mass of 5443.2 kg, how much does 100% have)
| Mass Flow from Thickened Activated Sludge = |  |  |  | 27939.1594 | kg/d |  | (Unitary method, if 4% has a mass of 1433 kg, how much does 100% have)
Parameters for Digester
| Y= |  |  |  | 0.08 | kg VSS/kg bCOD utilized | [5 empty] | Pg,1506,1507, Eq 13-12, 13-13
| b = |  |  |  | 0.03 | d-1
| S0= |  |  |  | 3895.281 | kg/d | (Combined BODC from Primary and Secondary Sludge)
| S= |  |  |  | 1558.1124 | kg/d | BODC after digestion based on percentage reduction of VSS
| Q= |  |  |  | 115.1492 | m3/d | Combined Flow rate
| SRT = |  |  |  | 20 | d
| PX = |  |  |  | 116.8584 | kg/d | Net Mass of Cell tissue produced per day
| VCH4 = |  |  |  | 759.9304 | m3/d
| VGAS = |  |  |  | 1169.1236 | m3/d | (Assuming 65% of biogas as methane)
| Biogas Mass = |  |  |  | 1309.4185 | kg/d | (Assuming density of biogas as 1.12 kg/m3)
vi. | Determine the mass quantities of gas and sludge after digestion.
Fixed Solids = TSSM - VSSM
| Fixed Solids = |  |  |  | 2595.5056 | kg/d
| TSSM in digested sludge= |  |  |  | 4209.1265 | kg/d
Mass Balance of Digested Output
| Mass IN = |  |  |  | 115149.1594 | kg/d
| Gas Produced = |  |  |  | 1309.4185 | kg/d
| Mass Out = |  |  |  | 113839.7409 | kg/d | (Solids and Liquid)
vii. | Determine the flowrate distribution between the supernatant at 0.5% solids and digested Sludge at 5% solids. Let X = TSS of Supernatant
| TSSC of Supernatant = |  |  |  | 0.5%
| TSSC of Digested Sludge = |  |  |  | 5%
Mass Flow of Supernatant + Mass Flow of Digested Solids = Mass Out
Let X be TSSM of Supernatant
{(X/0.005)+((4443-X)/0.05)}=123729
Solve for X
| X = |  |  |  | 164.7623 | kg/d
| TSSM of Supernatant = |  |  |  | 164.7623 | kg/d
| TSSM of Digested Sludge = |  |  |  | 4044.3643 | kg/d
| Supernatant Flowrate = |  |  |  | 32.9525 | m3/d
| Digested Sludge Flowrate = |  |  |  | 80.8873 | m3/d
viii. | Establish the characteristics of the recycled flow
| Flowrate = |  |  |  | 32.9525 | m3/d
| BODM of Supernatant = |  |  |  | 32.9525 | kg/d
| TSSM of Supernatant = |  |  |  | 164.7623 | kg/d
f. | Sludge Dewatering
i. | Operating Parameters for centrifuge :
| Sludge cake = |  |  |  | 22% | solids
| Specific gravity of sludge = |  |  |  | 1.123
| Solids capture = |  |  |  | 60%
| Centrate BODC = |  |  |  | 2000 | mg/L
| Density of Water = |  |  |  | 1000 | kg/m3
ii. | Determine the Sludge-cake characteristics.
| Solids = |  |  |  | 2426.6186 | kg/d
| Flow rate = |  |  |  | 9.822 | m3/d
iii. | Determine the Centrate Characteristics
| Flowrate = |  |  |  | 71.0653 | m3/d
| BODM = |  |  |  | 142.1306 | kg/d
| TSSM = |  |  |  | 1617.7457 | kg/d
g. | Prepare a summary table of the recycle flows and waste characteristics for the first iteration
| Operation | Flowrate, m3/d | BODM, kg/d | TSSM, kg/d
| Gravity Thickener | 66.69 | 496.9692 | 923.4
| Flotation Thickener | 193.8002 | 97.4207 | 155.2176
| Digester Supernatant | 32.9525 | 32.9525 | 164.7623
| Centrate | 71.0653 | 142.1306 | 1617.7457
| Totals | 364.508 | 769.473 | 2861.1255